## README
ADC Master Workbook — Australian Data Centre Dashboard / 澳洲数据中心数据看板主数据表
HOW THIS WORKBOOK IS USED / 使用说明
1. This workbook is the single source of truth. The website reads JSON that scripts/build_data.py generates from the NEWEST file in data/source/ (by the YYYYMMDD[_HHMM] timestamp in the filename).
本表是唯一数据源。网站读取的 JSON 由 scripts/build_data.py 从 data/source/ 中文件名时间戳最新的一份自动生成。
2. To update: run python scripts/new_version.py (copies this file to data/archive/ and creates a new time-stamped copy), edit the new copy, then git commit + push. GitHub Actions rebuilds and redeploys the site.
更新流程：运行 python scripts/new_version.py（旧版归档到 data/archive/，并生成新的时间戳副本）→ 编辑新副本 → git commit + push → GitHub Actions 自动重建并发布。
3. Do NOT rename sheet tabs or header cells — the build script looks them up by name. Add rows freely; add new columns at the right end (they are passed through to JSON automatically).
请勿重命名工作表或表头；可自由增加行；新增列请加在最右侧（会自动带入 JSON）。
4. Cells with several values (sources, tenants, overlap_with) use ' ¦ ' or ', ' as the separator — see each sheet's header note.
5. Every fact row should carry at least one URL in its sources column and a last_verified date.
SHEETS / 工作表
Meta — editable site metadata (titles, disclaimer, national narrative, map defaults) as key/value pairs
Facilities — one row per data centre / campus (map + tables)
Operators — one row per operator / developer / investor (stakeholder dashboard)
OperatorMoves — dated 'latest moves' per operator (join key: operator_id)
Market — national headline metrics for the KPI tiles
Reg_Jurisdictions — one row per jurisdiction (FED + 8 states/territories)
Reg_Steps — step-by-step connection pathway per jurisdiction; overlap_with lists jurisdictions whose process runs concurrently
Reg_Changes — dated recent regulatory changes per jurisdiction
Infrastructure — curated key infrastructure points (terminal stations, IX/carrier hotels, cable landing stations, Telstra exchanges, NBN POIs)
NBN_POI — all 121 NBN Points of Interconnect (separate map layer)
NewsSources — RSS feeds / Google News queries polled daily by scripts/fetch_news.py (enabled = TRUE/FALSE, filter_keywords optional)
Changelog — version log; add a line every time you create a new version
Stage taxonomy (Facilities.stage): Operational ¦ Under Construction ¦ Approved ¦ Planning
IT load figures are IT (critical) load in MW unless the notes say facility/grid power. Null = not publicly disclosed — do not guess.

## Meta
key | value | notes
site_title_en | Australian Data Centre Atlas | Site title
site_title_zh | 澳洲数据中心图谱
site_subtitle_en | Facilities, grid and fibre infrastructure, connection regulation, stakeholders and daily news
site_subtitle_zh | 设施分布、电网与光纤基础设施、并网监管、行业参与者及每日新闻
organisation | MAI Capital | Shown in footer
data_as_of | 2026-10-07 | Displayed as 'Data as of'
disclaimer_en | Compiled from public sources for research purposes. Capacity is IT load (MW) as disclosed by operators or reported by reputable media; a few projects publish only site or generation capacity and are marked in the capacity_basis column and excluded from IT-load totals. Undisclosed values are left blank rather than estimated. Verify before relying on any figure.
disclaimer_zh | 数据汇编自公开资料，仅供研究参考。容量口径为运营商披露或权威媒体报道的IT负载（MW）；少数项目仅公布场地或发电容量，已在 capacity_basis 列标注并从IT负载合计中剔除。未披露的数值留空而不作估算。引用前请自行核实。
national_summary_en | Australia's data-centre market at a glance (end-2025 operational base, October 2026 pipeline). - ~1.4-1.5 GW of operational IT load across ~160 facilities at end-2025; Sydney ~0.9 GW, Melbourne ~0.4 GW - AEMO tracks a 5.4 GW grid-connection pipeline of >5 MW projects (NSW ~60%, VIC ~40%); Transgrid alone reports ~20 GW of NSW connection enquiries - JLL puts the national pipeline at 16.2 GW and about A$155bn of investment; DC Byte counts 21.6 GW announced, ~3.1 GW committed - Credible operational capacity by 2030 is ~3.2 GW, so most of the announced pipeline will not be built - Policy, not capital, is now the binding constraint: Victoria's Sustainable Data Centre Action Plan, Queensland's move to State assessment and the Commonwealth's proposed mandatory standards all landed in late September 2026 | KPI panel narrative
national_summary_zh | 澳洲数据中心市场概览（2025年底在运存量，2026年10月管线口径）。 - 2025年底约160座设施、在运IT负载1.4–1.5 GW，悉尼约0.9 GW、墨尔本约0.4 GW - AEMO跟踪的5 MW以上并网申请管线为5.4 GW（新州约六成、维州约四成）；仅Transgrid一家即收到约20 GW的接入咨询 - JLL测算全国管线16.2 GW、投资约1,550亿澳元；DC Byte统计公告总量21.6 GW，已落实约3.1 GW - 2030年可信的在运容量约3.2 GW，公告管线绝大部分不会落地 - 约束已从资本转向政策：维州Sustainable Data Centre Action Plan、昆州改由州级SARA评估、联邦拟立强制标准，均在2026年9月下旬集中落地
overlap_notes_en | Large-load connection sits at the intersection of three Commonwealth regimes and two state-level tracks that run in parallel rather than in sequence. - The National Electricity Rules (Chapter 5 for transmission/large connections, Chapter 5A for distribution) govern the enquiry-application-offer-agreement sequence identically across NEM states, with AEMO approving advisory-matter performance standards and the AER policing connection charges and the RIT-T/RIT-D tests that decide whether augmentation is user-funded or socialised; WA (Access Code, WEM Rules) and the NT (Network Access Code, I-NTEM) replicate that structure under their own law with different regulators. - State planning consent is a separate, concurrent track: network operators will not finalise capacity or performance standards without it (Transgrid and TasNetworks make planning approval an explicit readiness criterion), and planning authorities in turn refer applications to the TNSP/DNSP for capacity advice. - State environmental licences (EPA licences for backup generation, water servicing agreements) overlap with the Commonwealth EPBC Act only where a matter of national environmental significance is triggered; bilateral agreements then let one assessment serve both governments while approval decisions remain separate. - FIRB approval for foreign proponents and SOCI Act obligations are purely Commonwealth but are being pulled into state processes — Transgrid lists FIRB approval among its capacity-retention tests, and states expect SOCI-grade security for government tenants. - The most significant 2026 development is the deliberate layering of energy policy: the AEMC/National Cabinet package (REGO surrender, firm capacity, AEMO registration, demand flexibility, full network cost recovery) will be legislated federally in 2027 through NER changes, while NSW, the ACT, Tasmania and SA are already writing equivalent or stricter conditions into planning consents and connection agreements; the Commonwealth has said states may go further but not weaker. - Where the two layers use different metrics, proponents should expect to satisfy both, and should treat every threshold announced in 2026 as provisional until regulations and final rule determinations are made. | Regulation tab: federal/state overlap explainer
overlap_notes_zh | 大负荷并网处于三个联邦制度与两个州级轨道的交汇点，各制度并行推进而非先后衔接。 - 《国家电力规则》（第5章适用于输电及大型接入，第5A章适用于配电）在各NEM州以相同方式规范咨询—申请—报价—协议流程，AEMO批准咨询事项的性能标准，AER监管接入费用及决定扩建由用户出资还是全体分摊的RIT-T/RIT-D测试；西澳（《接入守则》、WEM规则）与北领地（《网络接入守则》、I-NTEM）在各自法律下复制了该结构，仅监管者不同。 - 州规划许可是独立且同步的轨道：网络运营商在取得规划许可前不会最终确定容量或性能标准（Transgrid和TasNetworks将规划批准明确列为准备度标准），规划机构反过来也会将申请转介TNSP/DNSP征求容量意见。 - 州环境许可（备用发电的EPA许可、供水服务协议）仅在触发国家环境重要事项时才与联邦EPBC法重叠，此时双边协议允许一次评估同时服务两级政府，但审批决定仍相互独立。 - 外国业主的FIRB批准及SOCI法义务纯属联邦事项，但正被纳入州级程序——Transgrid把FIRB批准列为容量保留测试之一，各州也期望为政府租户提供SOCI级别的安全保障。 - 2026年最重要的变化是能源政策的刻意分层：AEMC/国家内阁方案（注销新建电源REGO、可靠容量、AEMO注册、需求灵活性、全额回收网络成本）将于2027年经NER修改在联邦层面立法，而新州、首都领地、塔州及南澳已在规划许可及接入协议中写入同等或更严格的条件；联邦已表明各州可以更严但不得更松。 - 两个层级采用不同指标时，业主应预期须同时满足两者，并在法规及最终规则裁定出台前，将2026年宣布的所有门槛视为暂定。
map_center_lat | -30.5 | Initial map view
map_center_lng | 141.5
map_zoom | 4.4
news_days_to_keep | 90 | fetch_news.py keeps items newer than this
news_max_items | 300

## Facilities
facility_id | name | operator | operator_id | owner | state | city_suburb | address | lat | lng | stage | type | year_announced | year_commissioned | it_load_mw_operational | it_load_mw_planned | site_area_ha | capex_aud_m | key_tenants | power_source_notes | cooling | certifications | description_en | description_zh | sources | last_verified | capacity_basis
cdc-beard | CDC Beard Campus (BE1) | CDC Data Centres | cdc | Infratil / CSC / Future Fund (CDC) | ACT | Beard, Canberra | Beard ACT 2620 | -35.3405 | 149.2182 | Under Construction | Enterprise/Government | 2023 |  |  | 39 |  |  | Undisclosed (government / cloud) | Evoenergy supply; third Canberra campus location. |  | Hosting Certification Framework (CDC group) | A 39MW first building on CDC's new Beard campus in Canberra's east, under construction to add a third sovereign availability zone in the ACT. | CDC在堪培拉东侧Beard新园区的首栋楼，IT负载39 MW，目前在建，建成后将成为CDC在首都领地的第三个主权可用区。 | https://cdc.com/locations/canberra/ | 2026-09-15 | IT load
cdc-fyshwick | CDC Fyshwick Campus (FY1-FY2) | CDC Data Centres | cdc | Infratil / CSC / Future Fund (CDC) | ACT | Fyshwick, Canberra | Fyshwick ACT 2609 | -35.3312 | 149.1752 | Operational | Enterprise/Government | 2014 | 2016 | 45 | 45 |  |  | Australian Government, Defence, cloud providers | Evoenergy supply; geographically diverse from Hume campuses. | air | Hosting Certification Framework Certified Strategic, ISO 27001 | CDC's 45MW Fyshwick campus, the second Canberra node providing metro diversity for Commonwealth and cloud workloads. | CDC在堪培拉的第二个节点，位于Fyshwick，IT负载45 MW，2016年投运，为联邦政府和云服务商提供与Hume园区异地的同城容灾。 | https://cdc.com/locations/canberra/ ¦ https://www.datacenters.com/cdc-data-centres-fyshwick-campus | 2026-09-15 | IT load
cdc-hume-campus-one | CDC Hume Campus One (HU1-HU3) | CDC Data Centres | cdc | Infratil / CSC / Future Fund (CDC) | ACT | Hume, Canberra | Sheppard Street precinct, Hume ACT 2620 | -35.3992 | 149.1662 | Operational | Enterprise/Government | 2007 | 2008 | 21 | 21 |  |  | Australian Government, Defence, Microsoft Azure Australia Central | Evoenergy 132kV/11kV; dual-campus separation from Hume Two and Fyshwick for government resilience. | air | Hosting Certification Framework Certified Strategic, ISO 27001, DISP | CDC's original Canberra campus (from 2008), the core of Australia's sovereign government hosting market and home to Microsoft's Azure Australia Central regions. | CDC最早的堪培拉园区，2008年投运，IT负载21 MW，是澳洲主权政府托管市场的核心资产，微软Azure Australia Central区域即部署于此。 | https://cdc.com/locations/canberra/ ¦ https://baxtel.com/data-center/cdc-hume-1 | 2026-09-15 | IT load
cdc-hume-campus-two | CDC Hume Campus Two (HU4-HU5) | CDC Data Centres | cdc | Infratil / CSC / Future Fund (CDC) | ACT | Hume, Canberra | Hume ACT 2620 | -35.4012 | 149.1705 | Operational | Enterprise/Government | 2016 | 2018 | 51 | 51 |  |  | Australian Government, Defence, hyperscale cloud | Evoenergy supply, separate feeders from Campus One. | air | Hosting Certification Framework Certified Strategic, ISO 27001 | CDC's second Hume campus, 51MW across two buildings, extending its government-certified Canberra footprint. | CDC在Hume的第二个园区，2018年投运，两栋楼合计51 MW，客户为联邦政府、国防部及超大规模云，与Campus One采用独立馈线供电。 | https://cdc.com/locations/canberra/ | 2026-09-15 | IT load
equinix-ca1 | Equinix CA1 Canberra | Equinix | equinix | Equinix (ex-Metronode) | ACT | Mitchell, Canberra | 51 Dacre Street, Mitchell ACT 2911 | -35.2172 | 149.1352 | Operational | Enterprise/Government | 2013 | 2014 |  |  |  |  | Australian Government agencies, carriers, enterprise | Evoenergy supply; former Metronode Canberra facility acquired by Equinix in 2018. | air | ISO 27001, PCI DSS, Hosting Certification Framework Certified Strategic | Equinix's Canberra IBX (ex-Metronode) in Mitchell, a government-certified colocation site providing carrier-neutral interconnection in the capital. | Equinix在堪培拉Mitchell的IBX，原为Metronode设施，2018年随收购并入；具备政府认证，是首都地区运营商中立的托管与互联节点。 | https://www.equinix.com/data-centers/asia-pacific-colocation/australia-colocation/canberra-data-centers/ca1 | 2026-09-15 | IT load
macquarie-ic5-canberra | Macquarie Data Centres Canberra Campus (IC4 / IC5 Bunker) | Macquarie Data Centres | macquarie-data-centres | Macquarie Technology Group (ASX: MAQ) | ACT | Canberra (south) - exact street not disclosed | Canberra Data Centre Campus, ACT (address undisclosed for security) | -35.395 | 149.165 | Operational | Enterprise/Government | 2018 | 2020 |  |  |  |  | Australian Federal Government (42% of agencies per Macquarie), hyperscalers | Evoenergy supply; MW undisclosed; coordinates approximate (campus location not published). | air | Uptime Tier III, ISO 27001, PCI DSS, SCEC, Hosting Certification Framework Certified Strategic | Macquarie's secure 'Bunker' campus in Canberra (IC4/IC5), a Certified Strategic sovereign facility hosting a large share of Commonwealth agency workloads. | Macquarie在堪培拉的"Bunker"高安全园区（IC4/IC5），2020年投运，属Certified Strategic级主权设施，承载相当比例的联邦机构工作负载；容量未公开。 | https://www.macquariedatacentres.com/data-centres/canberra/ic5/ | 2026-09-15 | IT load
nextdc-c1 | NEXTDC C1 Canberra | NEXTDC | nextdc | NEXTDC (ASX: NXT) | ACT | Bruce, Canberra | 19 Battye Street, Bruce ACT 2617 | -35.2442 | 149.0872 | Operational | Enterprise/Government | 2011 | 2012 | 4.4 | 4.4 |  |  | Australian Government agencies, enterprise | Evoenergy supply; N+1; purpose-built to PSPF/SCEC requirements. | air | ISO 27001, SOC 1/2 Type II, PCI DSS, DTA Certified Strategic, Climate Active | A 4.4MW government-grade colocation site in Bruce, small but strategically relevant as a Certified Strategic hosting facility for Commonwealth workloads. | NEXTDC在堪培拉Bruce的政府级托管设施，2012年投运，IT负载4.4 MW；规模虽小，但具备Certified Strategic认证，对联邦工作负载有战略价值。 | https://www.nextdc.com/data-centres/canberra-data-centres/c1-canberra | 2026-09-15 | IT load
stack-can01-hume | STACK Infrastructure CAN01 Hume | STACK Infrastructure | stack-infrastructure | STACK Infrastructure | ACT | Hume, Canberra | 1210 Tralee Street, Hume ACT 2620 | -35.4002 | 149.1652 | Under Construction | Colocation | 2022 |  |  | 28 |  |  | Government / hyperscale (target) | Evoenergy supply; 28MW planned; part of STACK's AU$1.3bn Australian buildout financing; status 'planned/in development' per market listings. | air |  | STACK's 28MW Canberra campus in the Hume data centre precinct, designed for government-grade and hyperscale tenants; delivery timing not publicly confirmed. | STACK在堪培拉Hume数据中心片区规划的28 MW园区，目标客户为政府级和超大规模租户，目前在建，交付时间尚未公开确认。 | https://www.datacentermap.com/australia/canberra/stack-infrastructure-can01a/ ¦ https://www.datacenterdynamics.com/en/news/stack-infrastructure-seeks-au13bn-for-australia-data-center-buildout/ | 2026-09-15 | IT load
aims-bella-vista | AIMS Capital Bella Vista Data Centre Campus | AIMS Capital Management |  | AIMS Capital Management | NSW | Bella Vista, Sydney | Bella Vista NSW 2153 (Hills Shire) | -33.7322 | 150.9502 | Planning | Hyperscale | 2026 | [5 empty] | Undisclosed | Details not public; project listed among 15 IDA-endorsed NSW data centres (Mar 2026). |  |  | A Hills Shire data centre campus sponsored by AIMS Capital Management and fast-tracked through the NSW Investment Delivery Authority in March 2026; capacity not yet disclosed. | AIMS Capital Management在悉尼Hills区Bella Vista发起的数据中心园区，2026年3月被新州投资交付局（IDA）纳入加速审批名单；容量尚未披露。 | https://w.media/nsw-moves-15-data-centres-worth-aud-51-9bn-into-ida-pipeline/ | 2026-09-15 | IT load
aws-eastern-creek | AWS Eastern Creek Campus (William Dean Street) | AWS | aws | Amazon | NSW | Eastern Creek, Sydney | William Dean Street, Eastern Creek NSW 2766 | -33.7992 | 150.8502 | Operational | Hyperscale campus (self-build) | 2020 | 2022 |  |  |  |  | AWS (ap-southeast-2) | Sydney West bulk supply area; multiple self-built buildings (1 William Dean A/B etc.); part of AWS's $13.2bn 2023-27 Australian investment; MW not disclosed. | air |  | Amazon's owned Western Sydney data centre cluster at Eastern Creek supporting the ap-southeast-2 region, built out in several phases since 2022. | 亚马逊在西悉尼Eastern Creek的自建数据中心集群，2022年起分期建设，支撑AWS ap-southeast-2区域；容量未公开。 | https://www.datacentermap.com/australia/sydney/amazon-aws-syd-eastern-creek/ ¦ https://www.datacenterdynamics.com/en/news/amazon-planning-new-data-centers-in-melbourne-and-sydney-australia/ | 2026-09-15 | IT load
aws-smeaton-grange-gregory-hills | AWS South-West Sydney Campus (Smeaton Grange / Gregory Hills) | AWS | aws | Amazon | NSW | Smeaton Grange / Gregory Hills, Sydney | 42A Bluett Drive & 52 Turner Road, Smeaton Grange NSW 2567; 43-61 Turner Road, Gregory Hills NSW 2557 | -34.0385 | 150.7605 | Under Construction | Hyperscale campus (self-build) | 2022 | 2019 |  |  | 9.4 |  | AWS (ap-southeast-2) | Endeavour Energy Macarthur network; existing SYD52 at Bluett Drive operational; 40MW building proposed at 52 Turner Rd; 9.4ha Gregory Hills site (27 generators) in early works with DC application to DPHI. | air |  | Amazon's second Sydney self-build cluster in the Macarthur region, with an operating site at Bluett Drive and further buildings at Turner Road progressing through NSW planning. | 亚马逊在悉尼西南Macarthur地区的第二个自建集群：Bluett Drive的SYD52已投运，Turner Road的后续楼栋正在走新州规划审批。 | https://www.theurbandeveloper.com/articles/amazon-plans-more-data-centres-in-sydney-and-melbourne ¦ https://www.theurbandeveloper.com/articles/amazon-lays-out-south-sydney-data-centre-plans | 2026-09-15 | IT load
airtrunk-kurri-kurri | AirTrunk Kurri Kurri (Hunter) Data Centre | AirTrunk | airtrunk | AirTrunk (site: former Hydro Aluminium smelter) | NSW | Loxford (Kurri Kurri), Hunter Valley | Hart Road, Loxford NSW 2326 (former Hydro Kurri Kurri smelter site) | -32.8268 | 151.4662 | Planning | Hyperscale | 2026 |  |  | 540 | 21 | 3700 | Undisclosed (AI/hyperscale) | 132kV grid connection with AirTrunk funding the full connection cost and a new substation; renewable supply to be procured from new New England REZ generation. No community water used for cooling - water limited to amenities. | Air cooling |  | AirTrunk lodged the Environmental Impact Statement for its 540MW Kurri Kurri data centre in September 2026, on the former Hydro Aluminium smelter site at Hart Road, Loxford, with capex now stated at about A$3.7 billion and a building footprint of roughly 44,220sqm over two storeys. A A$37 million community benefit package was announced on 16-17 September 2026, including a Community Energy Program offering A$200 a year off eligible households' electricity bills, and 350-plus ongoing jobs are forecast. The NSW Planning Portal still shows the application at 'Prepare EIS'; a public exhibition date has not been set. | AirTrunk 于 2026 年 9 月就 540 MW 的 Kurri Kurri 项目递交 EIS，场地为 Hart Road, Loxford 的原 Hydro Aluminium 冶炼厂用地，投资口径更新至约 37亿澳元，两层建筑约 44,220 ㎡、高约 16.8 m。供电按 132 kV 接入，接入成本与新建变电站由 AirTrunk 自行承担，并承诺采购 New England REZ 的新增可再生电源；冷却采用风冷，不取用社区供水，用水仅限生活设施。9 月 16–17 日同步公布 3,700万澳元社区回馈方案，含每户每年 200 澳元电费补贴的 Community Energy Program，其中 1,200万澳元用于体育设施与社区储能，预计长期岗位 350 个以上。NSW 规划门户仍显示处于 Prepare EIS 阶段，公展日期未定。 | https://www.datacenterdynamics.com/en/news/aluminum-smelter-site-in-australia-targeted-for-540mw-data-center-development/ ¦ https://www.newcastleherald.com.au/story/9327354/airtrunks-5-billion-kurri-kurri-data-centre-seeks-hunter-renewable-energy-partners/ ¦ https://www.planningportal.nsw.gov.au/major-projects/projects/kurri-kurri-data-centre | 2026-10-07 | IT load
airtrunk-lane-cove-mars-rd | AirTrunk Lane Cove West Expansion (Apollo Place / Mars Road) | AirTrunk | airtrunk | Blackstone / CPP Investments (AirTrunk) | NSW | Lane Cove West, Sydney | 3-4 Apollo Place & 87-91 Mars Road, Lane Cove West NSW 2066 | -33.8142 | 151.1438 | Planning | Hyperscale | 2026 |  |  | 140 |  |  | Undisclosed | Ausgrid North Shore network; requires EIS before community consultation (early planning stage as of Apr 2026). |  |  | A proposed five-storey, 140MW extension of AirTrunk's Sydney North footprint across two sites in the Lane Cove West business park, disclosed in council planning updates in 2026. | AirTrunk拟在Lane Cove West商务园两个地块上扩建140 MW、五层的悉尼北项目，2026年经市议会规划通报披露，仍处早期规划阶段。 | https://inthecove.com.au/2026/04/12/two-more-data-centres-planned-for-lane-cove-west-business-park/ | 2026-09-15 | IT load
airtrunk-syd1 | AirTrunk SYD1 Sydney West | AirTrunk | airtrunk | Blackstone / CPP Investments (AirTrunk) | NSW | Huntingwood, Sydney | 35 Huntingwood Drive, Huntingwood NSW 2148 | -33.7795 | 150.8592 | Operational | Hyperscale | 2016 | 2017 | 130 | 130 |  |  | Microsoft, Datacom, undisclosed hyperscalers | Diverse 132kV high-voltage feeds from Endeavour Energy network (Sydney West bulk supply area); design PUE 1.15. Capacity figure ~130MW per RenewMap/AirTrunk; combined SYD1+SYD3 campus 450MW+. | air / liquid-ready | ISO 27001, PCI DSS, ISAE 3402, SCEC Zone 3+ | AirTrunk's first Australian hyperscale campus, opened in 2017 in Huntingwood in Western Sydney and progressively expanded to around 130MW across 42 data halls, anchored by hyperscale cloud tenants. | AirTrunk在澳洲的首个超大规模园区，2017年在西悉尼Huntingwood投运，经多轮扩建至约130 MW、42个数据大厅，锁定租户为超大规模云服务商。 | https://airtrunk.com/location/syd1-sydney-west/ ¦ https://baxtel.com/data-center/airtrunk-sydney ¦ https://renewmap.com.au/resources/projects/nsw/datacentre/ | 2026-09-15 | IT load
airtrunk-syd2 | AirTrunk SYD2 Sydney North | AirTrunk | airtrunk | Blackstone / CPP Investments (AirTrunk) | NSW | Lane Cove West, Sydney | Sirius Road, Lane Cove West NSW 2066 | -33.8168 | 151.1462 | Operational | Hyperscale | 2019 | 2021 | 120 | 158 | 3.95 |  | Undisclosed hyperscalers (reported Microsoft) | Ausgrid 132kV supply; 70MW expansion (2023-24) lifted capacity to 120MW+; RenewMap lists 158MW. Local council notes further ~45MW approved-but-unbuilt stage at Apollo Place. | air | ISO 27001, PCI DSS, ISAE 3402 | AirTrunk's North Shore hyperscale facility in the Lane Cove West business park, opened 2021 and expanded by 70MW in 2023-24 to more than 120MW, giving hyperscalers a second Sydney availability zone away from the western cluster. | AirTrunk在悉尼北岸Lane Cove West商务园的超大规模设施，2021年投运，2023–24年扩容70 MW至120 MW以上，为云巨头提供独立于西悉尼集群的第二可用区。 | https://airtrunk.com/70-megawatt-expansion-underway-at-airtrunk-syd2/ ¦ https://inthecove.com.au/2026/04/12/two-more-data-centres-planned-for-lane-cove-west-business-park/ | 2026-09-15 | IT load
airtrunk-syd3 | AirTrunk SYD3 Sydney West | AirTrunk | airtrunk | Blackstone / CPP Investments (AirTrunk) | NSW | Huntingwood, Sydney | Huntingwood Drive precinct (adjacent SYD1), Huntingwood NSW 2148 | -33.7812 | 150.8615 | Under Construction | Hyperscale | 2023 | 2025 |  | 400 |  | 1300 | Undisclosed hyperscalers | Adjacent to Sydney West 330/132kV bulk supply point; initially filed at 320MW (2024), now tracked at 400MW (ITK/RenewMap). Bouygues awarded ~$1.3bn build contract. Design PUE 1.15, ~80% lower water use than conventional. | hybrid (liquid-ready) | ISO 27001 (AirTrunk group) | Seven-storey, ~123,000 sqm hyperscale build next to SYD1 that AirTrunk bills as the largest independent hyperscale data centre in APJ; first phases energised 2025 with the campus scaling toward 400MW. | 紧邻SYD1的七层、约12.3万平方米超大规模项目，AirTrunk称之为亚太及日本地区最大的独立超大规模数据中心；首期2025年通电，园区规划容量400 MW。 | https://airtrunk.com/airtrunk-syd3-is-expanding/ ¦ https://www.datacenterdynamics.com/en/news/airtrunk-files-to-develop-320mw-campus-in-sydney-australia/ ¦ https://itkservices3.com/background/data_centres_australia_top10_construction | 2026-09-15 | IT load
airtrunk-syd4-summit | AirTrunk SYD4 'Summit at Kemps Creek' | AirTrunk | airtrunk | AirTrunk (conditional acquisition from ISPT/IFM Investors) | NSW | Kemps Creek, Sydney | 706-752 Mamre Road, Kemps Creek NSW 2178 | -33.8598 | 150.7912 | Planning | Hyperscale | 2025 |  |  | 1200 | 52 | 5000 | Undisclosed hyperscalers | Up to four on-site substations planned within Mamre Road precinct (Endeavour Energy / Transgrid West Sydney network); 846-852 diesel backup generators; 100% renewables commitment by 2030. SEARS filed Sep 2025 by ISPT vehicle (KNBDC/Plan Project Management); EIS on exhibition 2026 with EPA raising information gaps and strong local objections; IDA-endorsed Mar 2026. | hybrid (liquid-ready) |  | A 52-hectare, six-building campus on Mamre Road filed by ISPT and being acquired by AirTrunk as 'SYD4'; at 1-1.2GW it would be Australia's first gigawatt-scale data centre campus but is still working through NSW state assessment. | 位于Kemps Creek Mamre Road的52公顷、六栋楼园区，由ISPT申报，AirTrunk有条件收购并命名为SYD4；规划1–1.2 GW，有望成为澳洲首个吉瓦级数据中心园区，目前仍在新州州级审批中。 | https://www.datacenterdynamics.com/en/news/airtrunk-set-to-buy-planned-1gw-data-center-site-in-western-sydney-australia/ ¦ https://ia.acs.org.au/article/2026/concern-over-australia-s-most-power-hungry-data-centre.html ¦ https://www.datacenterdynamics.com/en/news/plans-filed-for-1gw-data-center-campus-in-sydney-australia/ | 2026-09-15 | IT load
cdc-eastern-creek | CDC Eastern Creek Campus (EC1-EC6) | CDC Data Centres | cdc | Infratil / Commonwealth Superannuation Corp / Future Fund (CDC) | NSW | Eastern Creek, Sydney | 17 Roberts Road, Eastern Creek NSW 2766 | -33.7962 | 150.8562 | Operational | Hyperscale | 2018 | 2019 |  | 230 | 15 |  | Australian Government / Defence, Microsoft, enterprise | Transmission-grade 132kV connection (Sydney West bulk supply); EC1 6MW, EC2 13MW, EC4 ~78MW operational; EC5 & EC6 (~108MW IT each per ITK) under construction, campus total ~230MW. | air / liquid-capable | Hosting Certification Framework Certified Strategic, ISO 27001, DISP | CDC's Sydney flagship on the former HP site at Eastern Creek: four operating buildings with EC5/EC6 under construction, taking the government-certified campus toward ~230MW. | CDC在悉尼的旗舰园区，位于Eastern Creek原HP用地，四栋楼在运、EC5/EC6在建，园区满建约230 MW，具备政府认证。 | https://cdc.com/locations/sydney/ ¦ https://baxtel.com/data-center/cdc-eastern-creek-sydney-campus ¦ https://itkservices3.com/background/data_centres_australia_top10_construction | 2026-09-15 | IT load
cdc-marsden-park | CDC Marsden Park Campus | CDC Data Centres | cdc | Infratil / CSC / Future Fund (CDC) | NSW | Marsden Park, Sydney | Marsden Park Industrial Precinct (Hollinsworth Road area), Marsden Park NSW 2765 | -33.7082 | 150.8385 | Under Construction | Hyperscale | 2024 |  |  | 504 | 20.1 | 1400 | Undisclosed hyperscalers; reported front-runner for Anthropic 300-500MW Australian training contract | Dedicated 720MVA substation (Endeavour Energy/Transgrid); 40 generators; six four-storey buildings, scalable toward 1GW. State approval Nov 2025 (largest DC approval in southern hemisphere); early construction underway. Capex figure is initial-stage estimate. | hybrid (air + liquid) | Hosting Certification Framework Certified Strategic (CDC group) | CDC's 504MW, six-building AI/cloud campus in Marsden Park, approved by NSW in late 2025 and in early construction, with scope to reach 1GW. | CDC在Marsden Park的504 MW、六栋楼AI及云园区，2025年底获新州批准，已进入早期施工，远期可扩至1 GW。 | https://w.media/nsw-govt-approves-cdcs-504-mw-campus-in-sydney/ ¦ https://www.datacenterdynamics.com/en/news/cdc-breaks-ground-on-504mw-campus-in-sydney/ ¦ https://certifiedstrategic.com/insights/anthropic-australia-data-centre-cdc-frontrunner-500mw | 2026-09-15 | IT load
dci-cbr01-jerrabomberra | DCI CBR01 Canberra (Jerrabomberra) | DCI Data Centers | dci-data-centers | Brookfield Infrastructure (DCI) | NSW | Jerrabomberra (Queanbeyan), near Canberra | Poplars Innovation Precinct, Jerrabomberra NSW 2619 | -35.3722 | 149.2098 | Under Construction | Enterprise/Government | 2021 |  |  | 20 | 4 |  | Commonwealth government cloud workloads (target) | New Essential Energy 132kV line under multi-party agreement; Tier III / SCEC Zone 3 design; originally targeted RFS 2024, still listed as 'developing' by DCI in 2026. | air (high-efficiency) | Uptime Tier III (design), SCEC Zone 3 (design) | A 20MW, eight-hall secure 'cloud edge' facility on the NSW side of the Canberra border, built to give Commonwealth cloud workloads supply-chain and geographic diversity from the Hume/Fyshwick cluster. | DCI在堪培拉边界新州一侧Jerrabomberra在建的20 MW、八个数据大厅高安全"云边缘"设施，为联邦云工作负载提供与Hume/Fyshwick集群不同的供应链和地理冗余。 | https://www.datacenterdynamics.com/en/news/dci-data-centers-to-build-20mw-data-center-in-canberra-australia/ ¦ https://dcidatacenters.com/locations/ | 2026-09-15 | IT load
dci-syd-eastern-creek | DCI Data Centers Sydney (SYD01 / SYD02 / SYD03) | DCI Data Centers | dci-data-centers | Brookfield Infrastructure (DCI) | NSW | Eastern Creek, Sydney | 90 Peter Brock Drive, Eastern Creek NSW 2766 | -33.8012 | 150.8562 | Operational | Hyperscale | 2018 | 2020 | 11 | 65 |  | 400 | Hyperscale cloud, managed service providers | Endeavour Energy supply; SYD01 11MW live; SYD02 (36MW, AU$400m) and SYD03 in development on the same site, targeting ~65MW campus total. | air | Uptime Tier III, ISO 27001 | Brookfield-backed DCI's Eastern Creek campus: an 11MW first building live since 2020 with SYD02/SYD03 under development toward roughly 65MW for hyperscale and MSP customers. | Brookfield旗下DCI的Eastern Creek园区，首栋SYD01（11 MW）2020年投运，SYD02/SYD03在开发中，园区目标约65 MW，客户为超大规模云和托管服务商。 | https://www.datacenterdynamics.com/en/news/dci-build-au400-million-sydney-data-center/ ¦ https://dcidatacenters.com/locations/ | 2026-09-15 | IT load
digico-syd1-ultimo | DigiCo SYD1 Ultimo (ex-Global Switch Sydney) | DigiCo Infrastructure REIT | digico | DigiCo Infrastructure REIT (ASX: DGT, HMC Capital) | NSW | Ultimo, Sydney | 390-422 Harris Street & 273 Pyrmont Street, Ultimo NSW 2007 | -33.8772 | 151.1962 | Operational | Colocation | 2000 | 2001 | 42.5 | 88 |  | 605 | Carriers, financial services, cloud on-ramps, enterprise | Ausgrid CBD-fringe 132kV/33kV; $605m 'roof raise' to double IT load to 88MW (SSD on exhibition 2025). | air | ISO 27001, PCI DSS | The former Global Switch Sydney East/West campus in Ultimo, acquired by DigiCo for $1.9bn, with a $605m plan to lift IT capacity from 42.5MW to 88MW by adding floors to both buildings. | 位于Ultimo的原Global Switch悉尼东/西园区，2001年投运，DigiCo以19亿澳元收购；计划投资6.05亿澳元对两栋楼加层，将IT容量从42.5 MW提升至88 MW。 | https://www.theurbandeveloper.com/articles/digico-upgrade-sydney-ultimo-syd1-global-switch-data-centre ¦ https://www.digi-co.com.au/location/sydney-syd1/ | 2026-09-15 | IT load
digital-realty-erskine-park | Digital Realty Erskine Park Campus (SYD10/SYD11/SYD14) | Digital Realty | digital-realty | Digital Realty (NYSE: DLR) | NSW | Erskine Park, Sydney | 1-12 & 13-23 Templar Road and 16 Lockwood Road, Erskine Park NSW 2759 | -33.8122 | 150.8005 | Operational | Colocation | 2010 | 2011 |  | 250 | 16.2 |  | Hyperscale cloud, enterprise, carriers | Endeavour Energy 132kV; 2020 acquisition of two Erskine Park/Horsley Park parcels (16.2ha) for a campus of up to 250MW; SYD11 ~19MW. | air | ISO 27001, PCI DSS, SOC 1/2 | Digital Realty's long-standing Western Sydney campus on Templar Road, being expanded via adjacent Erskine Park and Horsley Park land toward a 250MW multi-building footprint. | Digital Realty在Templar Road经营多年的西悉尼园区，2011年投运，正借助毗邻的Erskine Park和Horsley Park地块扩建为满建250 MW的多楼园区。 | https://www.itnews.com.au/news/digital-realty-to-build-250mw-data-centre-campus-in-western-sydney-557912 ¦ https://www.digitalrealty.com/data-centers/asia-pacific/sydney/syd11 | 2026-09-15 | IT load
equinix-sy1-sy4-mascot | Equinix SY1-SY4 Mascot / Alexandria Cluster | Equinix | equinix | Equinix (NASDAQ: EQIX) | NSW | Mascot / Alexandria, Sydney | 639 Gardeners Road, Mascot NSW 2020 and 47 Bourke Road, Alexandria NSW 2015 | -33.9218 | 151.1878 | Operational | Colocation | 2000 | 2000 |  |  |  |  | Southern Cross Cable, carriers, IX peering, cloud on-ramps | Ausgrid supply; legacy campus with >20 years of incremental expansion (MW not disclosed). | air | ISO 27001, PCI DSS, SOC 1/2 | Equinix's original Sydney campus and cable-landing/interconnection hub for the Southern Cross and other trans-Pacific systems; small by modern MW standards but strategically central. | Equinix在悉尼的原始园区，2000年起运营，是Southern Cross等跨太平洋海缆的登陆与互联枢纽；容量按当前标准不大，但战略地位关键。 | https://www.equinix.com/data-centers/asia-pacific-colocation/australia-colocation/sydney-data-centers ¦ https://www.datacentermap.com/australia/sydney/ | 2026-09-15 | IT load
equinix-sy5 | Equinix SY5 Alexandria | Equinix | equinix | Equinix (NASDAQ: EQIX) | NSW | Alexandria, Sydney | Unit B, 200 Bourke Road, Alexandria NSW 2015 | -33.9147 | 151.1952 | Operational | Colocation | 2018 | 2019 | 54 | 54 |  |  | Cloud on-ramps, carriers, enterprise, subsea cable operators | Ausgrid 132kV; multiple expansion phases (latest AU$66m); 100% renewable via Equinix procurement. | air | ISO 27001, PCI DSS, SOC 1/2, Uptime-aligned | Equinix's largest Sydney IBX, a ~54MW retail colocation campus in Alexandria that anchors Sydney's densest interconnection ecosystem. | Equinix在悉尼最大的IBX，位于Alexandria，约54 MW，2019年投运，是悉尼互联生态最密集的零售托管园区。 | https://www.equinix.com/data-centers/asia-pacific-colocation/australia-colocation/sydney-data-centers/sy5 ¦ https://w.media/equinix-completes-au66-million-expansion-for-sy5-data-centre/ ¦ https://renewmap.com.au/resources/projects/nsw/datacentre/ | 2026-09-15 | IT load
equinix-sy9x-sy10x | Equinix xScale SY9x / SY10x Rosehill | Equinix (xScale) | equinix | PGIM Real Estate (80%) / Equinix (20%) JV | NSW | Rosehill, Sydney | Grand Avenue / James Ruse Drive precinct, Rosehill NSW 2142 | -33.8222 | 151.0232 | Operational | Hyperscale | 2021 | 2022 |  | 55 |  | 775 | Undisclosed hyperscalers (AWS/Azure-type) | Endeavour Energy supply in Rosehill; 55MW+ combined across two buildings; SY9x opened 2022, SY10x follow-on. | air | ISO 27001 (Equinix) | Equinix and PGIM's first Australian xScale hyperscale JV, two buildings at Rosehill totalling 55MW+ for large cloud deployments adjacent to the retail IBX ecosystem. | Equinix与PGIM在澳洲的首个xScale超大规模合资项目，位于Rosehill，两栋楼合计55 MW以上，SY9x于2022年投运，面向云巨头的大规模部署，并紧邻Equinix零售IBX生态。 | https://www.arnnet.com.au/article/1254911/equinix-plans-two-new-sydney-data-centres-through-775m-joint-venture.html ¦ https://www.datacenterdynamics.com/en/news/equinix-and-pgim-launch-hyperscale-facility-in-sydney/ | 2026-09-15 | IT load
fujitsu-western-sydney | Fujitsu Western Sydney Data Centre | Fujitsu DCs (Next Capital) | fujitsu-au-dc-next-capital | Fujitsu | NSW | Greystanes, Sydney | Greystanes NSW 2145 (Western Sydney Employment Hub) | -33.8222 | 150.9442 | Operational | Enterprise/Government | 2011 | 2013 |  |  |  |  | Government agencies, enterprise outsourcing clients | Endeavour Energy supply; MW undisclosed (third-party listings cite up to 92MW power capacity, treated as unverified). | air | ISO 27001, Hosting Certification Framework Certified Strategic | Fujitsu's flagship Australian Tier III facility at Greystanes, a government-certified enterprise data centre that complements its Homebush and North Ryde sites. | Fujitsu在澳洲的旗舰Tier III设施，位于Greystanes，2013年投运，具备政府认证，与其Homebush和North Ryde站点互补；容量未公开。 | https://www.datacentermap.com/australia/sydney/ | 2026-09-15 | IT load
lehr-glendenning-road | Glendenning Road Data Centre (LCI) | Lehr Consultants International (proponent) |  | Undisclosed end user | NSW | Glendenning, Sydney | Glendenning Road, Glendenning NSW 2761 | -33.7462 | 150.8562 | Approved | Hyperscale campus (self-build) | 2025 |  |  | 193.6 | 10.43 | 2170 | Undisclosed hyperscaler (LCI has acted for Microsoft on other Sydney sites) | Approximately 235MW maximum electrical demand against 193.6MW IT load; three internal substations and 97 standby diesel generators approved. |  |  | SSD-73761707 was determined on 14 September 2026, approving three five-storey data centre buildings totalling 50,233sqm on 10.43ha at 2 Glendenning Road, Glendenning: 193.6MW IT load (DC01 79.2MW, DC02 35.2MW, DC03 79.2MW), ~235MW maximum demand and A$2.17 billion capex, delivered in three stages. Lehr Consultants International is the formal proponent; multiple outlets report AWS as the end user, but this is not confirmed in the application. Blacktown City Council objected during exhibition. | SSD-73761707 于 2026 年 9 月 14 日获批：2 Glendenning Road, Glendenning 的 10.43 公顷地块建三栋五层厂房，合计 50,233 ㎡、最高约 43.2 m，IT负载 193.6 MW（DC01 79.2 MW、DC02 35.2 MW、DC03 79.2 MW），最大需量约 235 MW，造价 21.7亿澳元，分三期交付，配 3 座内部变电站与 97 台柴发。申请主体为 Lehr Consultants International，多家媒体指向 AWS 为最终用户，官方文件未予确认。Blacktown City Council 在公展期提出反对。项目预计带来约 1,076 个建设岗位、106 个运营岗位。 | https://www.planningportal.nsw.gov.au/major-projects/projects/glendenning-road-data-centre ¦ https://w.media/nsw-moves-15-data-centres-worth-aud-51-9bn-into-ida-pipeline/ | 2026-10-07 | IT load
goodman-project-apollo | Goodman Project Apollo Macquarie Park | Goodman Group | goodman | Goodman Group | NSW | Macquarie Park, Sydney | 4-10 Talavera Road, Macquarie Park NSW 2113 | -33.7738 | 151.1202 | Approved | Hyperscale | 2024 |  |  | 135 |  | 1370 | Undisclosed | Ausgrid Macquarie Park network; grid with diesel backup and Li-ion batteries; evaporative cooling towers. SSD approved 2 Sep 2026 after 541-day assessment. | hybrid (evaporative) |  | A 135MW, eight-hall, five-storey data centre approved in September 2026 on Talavera Road, making Macquarie Park one of Sydney's densest data centre precincts. | Goodman在Macquarie Park Talavera Road的135 MW数据中心，五层、八个数据大厅，2026年9月获SSD批准，Macquarie Park由此成为悉尼数据中心密度最高的片区之一。 | https://www.datacenterdynamics.com/en/news/goodman-group-gets-green-light-for-135mw-data-center-in-northern-sydney-australia/ ¦ https://w.media/goodman-wins-approval-for-135mw-macquarie-park-data-centre/ | 2026-09-15 | IT load
goodman-project-atlas | Goodman Project Atlas Eastern Creek | Goodman Group | goodman | Goodman Group / Goodman Australia Partnership | NSW | Eastern Creek, Sydney | 10 Roberts Road, Eastern Creek NSW 2766 | -33.7942 | 150.8582 | Planning | Hyperscale | 2026 |  |  | 500 | 17 | 5500 | Undisclosed (AI/hyperscale) | On-site substation off Sydney West 330/132kV BSP; DCCEEW requiring Goodman to demonstrate new renewable supply. SEARS Jan 2026 (former Coles DC site next to CDC); IDA-endorsed Mar 2026; targeting 2029. | liquid-ready |  | Goodman's largest Australian data centre proposal: a ~$5.5bn, 500MW two-building 'AI factory' campus on the former Coles distribution centre at Eastern Creek, awaiting state determination. | Goodman在澳洲最大的数据中心提案：在Eastern Creek原Coles配送中心地块上开发约55亿澳元、500 MW的双楼"AI工厂"园区，目前待州政府审批。 | https://www.datacenterdynamics.com/en/news/goodman-files-to-develop-90mw-data-center-campus-in-sydney-australia-2/ ¦ https://www.forbes.com.au/news/innovation/nsw-pushes-goodman-to-back-fresh-power-for-5-5-billion-ai-factory/ | 2026-09-15 | IT load
goodman-project-mars | Goodman Project Mars Lane Cove West | Goodman Group | goodman | Goodman Group | NSW | Lane Cove West, Sydney | 12 Mars Road, Lane Cove West NSW 2066 | -33.8152 | 151.1422 | Withdrawn | Hyperscale | 2025 |  |  | 90 |  | 1200 | Undisclosed | Ausgrid North Shore network; SSD on public exhibition to 28 Apr 2026 with significant local objection. |  |  | Goodman formally withdrew the State Significant Development application for the 90MW, ~A$1.2 billion data centre at 12 Mars Road, Lane Cove West in the week of 28 September 2026. The exhibition drew 374 submissions with only nine supportive; the nearest homes are 20m away and a primary school 160m away. Goodman said the policy and regulatory environment for large-scale data centre development had evolved significantly since it began the process in March 2025. | Goodman 于 2026 年 9 月 28 日当周正式撤回 12 Mars Road, Lane Cove West 的 SSD 申请，项目规模 90 MW、投资约 12亿澳元。公展期共收到 374 份意见，仅 9 份支持；场地距最近住宅 20 m、距小学 160 m。公司表示，自 2025 年 3 月启动规划以来，联邦与州层面针对大型数据中心的政策与监管环境已明显收紧，并称已考虑社区意见。Goodman 在悉尼的其余管线继续推进——Macquarie Park 135 MW、Guildford West 126 MW、前 ABC 影棚 90 MW、Mascot 旧 Eaton 仓库 90 MW。 | https://w.media/goodman-files-application-for-project-mars-90mw-data-center-campus-at-lane-cove-west-sydney/ ¦ https://inthecove.com.au/2026/04/08/goodman-lodges-mars-road-lane-cove-west-data-centre-development-application/ | 2026-10-07 | IT load
goodman-project-pluto | Goodman Project Pluto Guildford West | Goodman Group | goodman | Goodman Group | NSW | Guildford West, Sydney | 132 McCredie Road, Guildford West NSW 2161 | -33.8472 | 150.9722 | Approved | Hyperscale | 2023 |  |  | 68 | 7.17 | 1110 | Undisclosed | Stage 1 (34MW) direct from Transgrid Guildford transmission substation; Stage 2 (34MW) via new on-site substation on Endeavour network. Approved Jul 2026; earlier iterations cited 126MW/$2.5bn. | water-cooled (PUE 1.27-1.32) |  | Goodman's former-Castrol-site data centre at Guildford West, approved in July 2026 as a two-stage 68MW, nine-hall facility with power staged to grid availability. | Goodman在Guildford West原Castrol地块的数据中心，2026年7月获批，分两期建设68 MW、九个数据大厅，供电按电网容量释放进度分期到位。 | https://w.media/nsw-approves-goodmans-aud-1-1bn-project-pluto-data-centre-in-western-sydney/ ¦ https://www.datacenterdynamics.com/en/news/goodman-to-build-126mw-data-center-campus-on-former-castrol-hq-in-sydney-australia/ | 2026-09-15 | IT load
goodman-syd01-artarmon | Goodman SYD01 Artarmon | Goodman Group | goodman | Goodman Group | NSW | Artarmon, Sydney | 2-8 Lanceley Place, Artarmon NSW 2064 | -33.8102 | 151.1792 | Under Construction | Hyperscale | 2024 |  |  | 61 | 1.4 |  | Undisclosed | 90MW utility feed from Ausgrid; 61MW IT; Phase 1 12.2MW targeted Q2 2028; builder AW Edwards; ground broken Mar 2026. | liquid-ready |  | Goodman's first Australian self-developed data centre, on the former ABC TV studios in Artarmon, under construction with 61MW IT capacity and first phase due 2028. | Goodman在澳洲首个自主开发的数据中心，位于Artarmon原ABC电视台旧址，IT负载61 MW，2026年3月开工，首期预计2028年投运。 | https://www.datacenterdynamics.com/en/news/australias-goodman-breaks-ground-on-sydney-data-center/ ¦ https://au.goodman.com/data-centres/sydney/syd01 | 2026-09-15 | IT load
greensquaredc-syd1 | GreenSquareDC SYD1 Greater Western Sydney Campus | GreenSquareDC | greensquaredc | Partners Group (GreenSquareDC) | NSW | Bella Vista / Baulkham Hills, Sydney | Norwest / Bella Vista precinct, Hills Shire NSW 2153 | -33.7342 | 150.9542 | Under Construction | Hyperscale | 2023 |  |  | 100 |  |  | Sharon AI (anchor, SYD1 stage 1) | Endeavour Energy Hills network; Stage 2 (96MW) endorsed by Hills Shire Council Jan 2026 and IDA-endorsed Mar 2026; campus marketed as 100MW+; stage 1 build status not clearly disclosed. | liquid-ready (AI) |  | GreenSquareDC announced on 21 September 2026 a long-term contract with Nasdaq-listed Nvidia Cloud Partner Sharon AI for the first stage of SYD1 at 3 Brookhollow Avenue, Baulkham Hills — the campus's first anchor tenant. Sharon AI plans roughly 8,200 Nvidia Blackwell Ultra GPUs with initial operations targeted for Q4 2026. The campus combines a refurbished legacy building with new build; Stage 2 (80MW) was endorsed by the NSW Investment Delivery Authority in March 2026. | GreenSquareDC 于 2026 年 9 月 21 日宣布与纳斯达克上市的 Nvidia Cloud Partner Sharon AI 签订长期合同，锁定 SYD1 一期算力，为该园区首个锁定租户。SYD1 位于 3 Brookhollow Avenue（原 IBM 场地），由既有机房改造与新建楼栋组成；Sharon AI 计划部署约 8,200 颗 Nvidia Blackwell Ultra GPU，首批上线目标为 2026 年四季度。二期 80 MW 已于 2026 年 3 月获 NSW Investment Delivery Authority 支持。园区满建规模媒体报道为 110 MW，与此前 100 MW 口径存在差异，尚待核实。 | https://greensquaredc.com/news/greensquaredc-advances-1oomw-greater-western-sydney-campus-as-demand-for-data-centre-infrastructure-accelerates/ ¦ https://www.datacenterdynamics.com/en/news/partners-group-acquires-australian-data-center-firm-greensquaredc/ ¦ https://www.datacentermap.com/australia/sydney/greensquaredc-syd1/ | 2026-10-07 | IT load
ispt-julius-ave-north-ryde | ISPT Julius Avenue Data Centre North Ryde | ISPT | ispt | ISPT / IFM Investors | NSW | North Ryde, Sydney | 6-8 Julius Avenue, North Ryde NSW 2113 | -33.7962 | 151.1352 | Planning | Hyperscale | 2025 |  |  | 170 | 3.63 | 1800 | Undisclosed | On-site switching station, 72 x 3.2MW generators; Ausgrid North Ryde network. SSD exhibited 2025. |  |  | A $1.8bn, six-storey 170MW data centre proposed by ISPT on a long-held Riverside Corporate Park site, pivoting from office to data centre use. | ISPT在其长期持有的North Ryde Riverside Corporate Park地块上由办公开发改为数据中心，规划六层、170 MW，投资18亿澳元，目前处于规划阶段。 | https://www.datacenterdynamics.com/en/news/ispt-files-to-build-170mw-data-center-in-sydney-australia/ ¦ https://www.planningportal.nsw.gov.au/major-projects/projects/julius-avenue-data-centre | 2026-09-15 | IT load
leading-edge-wga1-wagga | Leading Edge DC WGA1 Wagga Wagga | Leading Edge DC | leading-edge-dc | Leading Edge Data Centres | NSW | Turvey Park, Wagga Wagga | Turvey Park, Wagga Wagga NSW 2650 | -35.1262 | 147.3612 | Operational | Edge | 2021 | 2022 |  |  |  | 2.7 | Regional enterprise, local government, carriers | Essential Energy distribution; prefabricated 30-75 rack modules. | air |  | A small prefabricated edge data centre in Wagga Wagga, part of Leading Edge DC's regional NSW network (Newcastle, Tamworth, Dubbo, Coffs Harbour) - strategically notable rather than MW-significant. | Leading Edge DC在Wagga Wagga的小型预制边缘数据中心，2022年投运，属其覆盖新州区域城市（Newcastle、Tamworth、Dubbo、Coffs Harbour）的网络之一，战略意义大于容量规模。 | https://www.datacenterdynamics.com/en/news/leading-edge-dc-gains-approval-for-data-center-in-wagga-wagga/ | 2026-09-15 | IT load
macquarie-ic3-macquarie-park | Macquarie Data Centres Macquarie Park Campus (IC2 / IC3 East / IC3 Super West) | Macquarie Data Centres | macquarie-data-centres | Macquarie Technology Group (ASX: MAQ) | NSW | Macquarie Park, Sydney | 17-23 Talavera Road, Macquarie Park NSW 2113 | -33.7722 | 151.1182 | Operational | Colocation | 2021 | 2012 |  | 63 |  |  | Australian Government agencies, hyperscale cloud, enterprise AI | Ausgrid supply; IC3 Super West raised from 32MW to 45MW (campus 50MW to 63MW); construction complete 2025, fit-out and phased commissioning 2025-26; AU$130m raised 2023. | hybrid (liquid-ready for AI) | Uptime Tier III, ISO 27001, PCI DSS, SCEC, Hosting Certification Framework Certified Strategic | Macquarie's sovereign colocation campus in Macquarie Park; the new IC3 Super West adds 45MW of AI-ready capacity, lifting the campus to 63MW. | Macquarie在Macquarie Park的主权托管园区，2012年起运营；新建的IC3 Super West新增45 MW面向AI的容量，园区总规模提升至63 MW。 | https://www.datacenterdynamics.com/en/news/macquarie-data-centres-to-increase-planned-capacity-for-upcoming-sydney-data-center/ ¦ https://www.macquariedatacentres.com/data-centres/sydney/macquarie-park-campus/ic3-super-west/ | 2026-09-15 | IT load
markham-oriordan-st-alexandria | Markham 22 O'Riordan Street Alexandria Data Centre | Markham Real Estate Partners |  | Markham Real Estate Partners | NSW | Alexandria, Sydney | 22 O'Riordan Street, Alexandria NSW 2015 | -33.9122 | 151.1932 | Planning | Colocation | 2024 |  |  | 38 | 0.74 |  | Undisclosed | Ausgrid inner-south network near Equinix SY cluster; SEARS Nov 2024; DCD-reported capex (AU$2bn) appears inconsistent with 38MW and is omitted. |  |  | A 38MW mixed-use data centre proposed by Markham on a former Mercedes-Benz body-shop site in Alexandria, adjacent to Sydney's key interconnection precinct. | Markham拟在Alexandria原Mercedes-Benz车身维修厂地块上建设38 MW混合用途数据中心，毗邻悉尼核心互联片区，目前处于规划阶段。 | https://www.datacenterdynamics.com/en/news/markham-files-for-38mw-data-center-in-sydney-australia/ ¦ https://www.planningportal.nsw.gov.au/major-projects/projects/22-oriordan-street-alexandria-data-centre | 2026-09-15 | IT load
mayfield-energy-precinct-newcastle | Mayfield Energy Precinct Data Centre (Port of Newcastle) | Undisclosed |  | Port of Newcastle / Newcastle Logistics Precinct proponents | NSW | Mayfield, Newcastle | Former Intertrade / BHP steelworks site, Mayfield NSW 2304 | -32.8952 | 151.7402 | Planning | Hyperscale | 2025 |  |  | 1000 |  |  | Undisclosed | Adjacent to Ausgrid/Transgrid Newcastle transmission and Port of Newcastle clean-energy precinct; listed as 1,000MW 'development' stage by RenewMap; limited public detail. |  |  | A gigawatt-scale data centre concept within the Mayfield clean-energy and logistics precinct at the Port of Newcastle, tracked by RenewMap but with sparse public disclosure. | Newcastle港Mayfield清洁能源与物流片区内的吉瓦级数据中心概念项目，RenewMap将其列为1,000 MW开发阶段项目，公开信息有限。 | https://renewmap.com.au/resources/projects/nsw/datacentre/ ¦ https://www.newcastleherald.com.au/story/8884008/mayfield-intertrade-site-to-become-a-logistics-precinct/ | 2026-09-15 | Site/grid power
microsoft-honeman-close | Microsoft Honeman Close Huntingwood Data Centre | Microsoft | microsoft | Microsoft | NSW | Huntingwood, Sydney | 6 Honeman Close, Huntingwood NSW 2148 | -33.7832 | 150.8562 | Approved | Hyperscale campus (self-build) | 2024 |  |  | 96 | 5.03 | 1260 | Microsoft Azure | Dedicated 132kV substation with three transformers, 47 diesel generators; six-storey building. SSD lodged May 2024 (via LCI), IDA-endorsed Mar 2026; capex figure is SSD estimated development cost (likely shell only). | air | Design targets: PUE 1.28, WUE 1.55 L/kWh | NSW DPHI determined SSD-58601963 on 1 October 2026, approving a 96MW IT load data centre across 40 data halls on five floors at 6 Honeman Close, Huntingwood, on a 5.03ha site, at A$1.26 billion capex. Conditions include a 1.28 PUE target, a 1.55 L/kWh WUE target, retention of 0.78ha of conservation area and ongoing noise, air-quality, energy and water monitoring. | NSW DPHI 于 2026 年 10 月 1 日核准 SSD-58601963：微软在 6 Honeman Close, Huntingwood 的 5.03 公顷地块建设 IT负载 96 MW 的数据中心，五层共 40 个机房，造价 12.6亿澳元。批复设定 PUE 1.28、WUE 1.55 L/kWh，要求保留并管理 0.78 公顷保育用地，并持续监测噪声、空气质量及能耗水耗。申请主体仍为 Lehr Consultants International。该项目过关与 Goodman 撤回 Lane Cove West 的 Project Mars 几乎同期，是新州新政策框架下首批获批的大型项目之一。 | https://www.datacenterdynamics.com/en/news/96mw-data-center-proposed-in-west-sydney-australia/ ¦ https://www.telecompaper.com/news/microsoft-submits-plans-for-third-self-build-data-centre-in-sydney--1500247 ¦ https://w.media/nsw-moves-15-data-centres-worth-aud-51-9bn-into-ida-pipeline/ | 2026-10-07 | IT load
microsoft-kemps-creek | Microsoft Kemps Creek Campus (SYD05/06/07) | Microsoft | microsoft | Microsoft | NSW | Kemps Creek, Sydney | 769 Mamre Road, Kemps Creek NSW 2178 | -33.8632 | 150.7882 | Under Construction | Hyperscale campus (self-build) | 2022 |  |  | 190 | 14.4 | 1300 | Microsoft Azure | Mamre Road precinct, Endeavour Energy network; ~96MW first stage expandable to 190MW; two two-storey buildings (65,355 sqm); builder AW Edwards; VPA with Penrith Council. | air (Microsoft standard) |  | Microsoft's $1.3bn self-build Azure campus at Kemps Creek, its largest owned facility in Australia, staged from ~96MW to 190MW. | 微软在Kemps Creek自建的Azure园区，投资13亿澳元，是其在澳洲最大的自有设施，首期约96 MW，可分期扩至190 MW，目前在建。 | https://www.datacenterdynamics.com/en/news/microsoft-confirms-plans-for-one-data-center-campus-in-sydney-drops-plans-for-another/ ¦ https://local.microsoft.com/blog/kemps-creek-datacentre-overview/ ¦ https://renewmap.com.au/resources/projects/nsw/datacentre/ | 2026-09-15 | IT load
microsoft-seven-hills | Microsoft Seven Hills (Station Road) Campus | Microsoft | microsoft | Microsoft | NSW | Seven Hills, Sydney | Station Road, Seven Hills NSW 2147 | -33.7742 | 150.9372 | Operational | Hyperscale campus (self-build) | 2021 | 2023 |  |  |  |  | Microsoft Azure | Endeavour Energy supply; Building 1 complete 2023 (FDC), Building 2 (Taylor) late 2024; further 'Station Road Data Centre Expansion' SSD lodged. | air |  | Microsoft's first self-built Sydney data centre campus, two buildings delivered 2023-24 with a further expansion in state assessment. | 微软在悉尼首个自建数据中心园区，两栋楼于2023–24年交付，后续扩建已进入州级评估。 | https://local.microsoft.com/blog/station-road-datacentres/ ¦ https://www.planningportal.nsw.gov.au/major-projects/projects/station-road-data-centre-expansion | 2026-09-15 | IT load
starwood-doma-telstra-minchinbury | Minchinbury AI Data Centre (Starwood / Doma / Telstra InfraCo) | Doma Infrastructure Group |  | Starwood Capital / Doma Infrastructure (land: Telstra InfraCo) | NSW | Minchinbury, Sydney | Telstra site, Minchinbury NSW 2770 | -33.7812 | 150.8332 | Under Construction | Hyperscale | 2025 |  |  | 62 |  |  | Undisclosed (carrier-neutral, hyperscale-ready) | Endeavour Energy; DA approved; construction from early 2026, RFS early Q1 2028; Tier III design. | liquid-ready (AI-optimised) | Uptime Tier III (design) | A 62MW AI-optimised, carrier-neutral data centre on Telstra land at Minchinbury, financed by Starwood and Doma with Telstra contributing land and connectivity. | 在Telstra位于Minchinbury的地块上建设的62 MW AI优化、运营商中立数据中心，由Starwood和Doma出资，Telstra提供土地和网络接入，目前在建。 | https://www.datacenterdynamics.com/en/news/starwood-doma-and-telstra-plan-62mw-data-center-in-sydney/ ¦ https://www.datacentermap.com/australia/sydney/telstra-minchinbury/ | 2026-09-15 | IT load
nextdc-s1 | NEXTDC S1 Sydney | NEXTDC | nextdc | NEXTDC (ASX: NXT) | NSW | Macquarie Park, Sydney | 4 Eden Park Drive, Macquarie Park NSW 2113 | -33.7746 | 151.1252 | Operational | Colocation | 2011 | 2013 | 16 | 16 |  |  | Enterprise, cloud on-ramps (AWS, Microsoft, Google, Oracle), carriers | Ausgrid 33kV/132kV supply; 100% renewable via NEXTDC procurement. | air | Uptime Tier III Design & Facility, ISO 27001, PCI DSS, DTA Certified Strategic | NEXTDC's first Sydney colocation facility and a key North Sydney interconnection hub with all major cloud on-ramps. | NEXTDC在悉尼的首座托管数据中心，位于Macquarie Park，2013年投运，IT负载16 MW，汇聚各大公有云接入点，是悉尼北部的重要互联枢纽。 | https://www.nextdc.com/data-centres/sydney-data-centres/s1-sydney | 2026-09-15 | IT load
nextdc-s2 | NEXTDC S2 Sydney | NEXTDC | nextdc | NEXTDC (ASX: NXT) | NSW | Macquarie Park, Sydney | 6 Eden Park Drive, Macquarie Park NSW 2113 | -33.7752 | 151.1258 | Operational | Colocation | 2016 | 2017 | 30 | 30 |  |  | Enterprise, government, cloud | Ausgrid supply; Uptime Tier IV certified. | air | Uptime Tier IV Gold (Operational Sustainability), ISO 27001, DTA Certified Strategic | A 30MW Tier IV colocation facility adjoining S1, one of only a handful of Uptime Tier IV Gold sites in Australia. | 紧邻S1的30 MW Tier IV托管设施，2017年投运，是澳洲少数获Uptime Tier IV Gold认证的站点之一。 | https://www.nextdc.com/data-centres/sydney-data-centres-colocation ¦ https://www.datacentermap.com/australia/sydney/ | 2026-09-15 | IT load
nextdc-s3 | NEXTDC S3 Sydney | NEXTDC | nextdc | NEXTDC (ASX: NXT) | NSW | Artarmon, Sydney | Artarmon NSW 2064 (Reserve Road / Herbert Street industrial precinct) | -33.8117 | 151.1832 | Operational | Colocation | 2019 | 2021 |  | 80 |  |  | Hyperscale cloud, enterprise, government | Ausgrid 132kV; RenewMap lists 80MW; NEXTDC does not disclose built MW per site. | air / liquid-ready | Uptime Tier IV Design & Facility, ISO 27001, DTA Certified Strategic | NEXTDC's flagship 80MW Sydney campus at Artarmon, opened 2021, designed to Tier IV and serving hyperscale and enterprise customers on the North Shore. | NEXTDC的悉尼旗舰园区，位于Artarmon，2021年投运，规划80 MW、按Tier IV设计，服务北岸的超大规模云和企业客户。 | https://www.nextdc.com/data-centres/sydney-data-centres-colocation ¦ https://renewmap.com.au/resources/projects/nsw/datacentre/ | 2026-09-15 | IT load
nextdc-s4 | NEXTDC S4 Sydney | NEXTDC | nextdc | NEXTDC (ASX: NXT) | NSW | Horsley Park, Sydney | Horsley Park NSW 2175 (Wallgrove Road precinct) | -33.8312 | 150.8505 | Under Construction | Hyperscale | 2021 |  |  | 350 |  |  | Undisclosed hyperscalers | Sydney West 330/132kV bulk supply area (Transgrid/Endeavour); planned capacity lifted from 300MW to 350MW; 124,000 sqm technical space. Ground broken Mar 2026 with Multiplex; IDA-endorsed Mar 2026. | hybrid (liquid-ready) | Uptime Tier IV (target) | NEXTDC's 350MW hyperscale campus at Horsley Park, land-banked in 2021 and finally under construction from March 2026 to serve hyperscale cloud and AI demand in Western Sydney. | NEXTDC在Horsley Park的350 MW超大规模园区，2021年购地储备，2026年3月正式开工，面向西悉尼的超大规模云和AI需求。 | https://www.nextdc.com/data-centres/sydney-data-centres/s4-sydney ¦ https://www.datacenterdynamics.com/en/news/australias-nextdc-breaks-ground-on-sydney-data-center/ | 2026-09-15 | IT load
nextdc-s5 | NEXTDC S5 Sydney (Innovation Hub) | NEXTDC | nextdc | NEXTDC (ASX: NXT) | NSW | Macquarie Park, Sydney | Macquarie Park NSW 2113 | -33.7762 | 151.1242 | Planning | Colocation | 2023 |  |  | 80 |  |  | Undisclosed | Ausgrid Macquarie Park network; 16,000 sqm technical space; IDA-endorsed Mar 2026 (State Significant Development). |  | Uptime Tier IV (target) | An 80MW+ Tier IV colocation and 'innovation hub' planned for Macquarie Park to extend NEXTDC's North Sydney availability zone. | NEXTDC规划在Macquarie Park建设的80 MW以上Tier IV托管及"创新中心"项目，用于扩充其悉尼北部可用区。 | https://www.nextdc.com/data-centres/sydney-data-centres/s5-sydney ¦ https://w.media/nsw-moves-15-data-centres-worth-aud-51-9bn-into-ida-pipeline/ | 2026-09-15 | IT load
nextdc-s6 | NEXTDC S6 Sydney (AI Factory) | NEXTDC | nextdc | NEXTDC (ASX: NXT) | NSW | Artarmon, Sydney | Adjacent to S3, Artarmon NSW 2064 | -33.8122 | 151.1838 | Operational | Colocation | 2024 | 2025 |  | 13.5 |  |  | Sovereign AI / GPU cloud customers | Shares Artarmon campus grid infrastructure with S3; 4,000 sqm technical space. | liquid (direct-to-chip) + air | Uptime Tier IV (progress to certification) | Marketed as Australia's first purpose-built AI-factory data centre, a 13.5MW liquid-cooled facility beside S3 targeting GPU-dense sovereign AI workloads. | NEXTDC定位为澳洲首个专建AI工厂的数据中心，位于S3旁，13.5 MW、采用液冷，2025年投运，面向高密度GPU和主权AI工作负载。 | https://www.nextdc.com/data-centres/sydney-data-centres/s6-sydney | 2026-09-15 | IT load
nextdc-s7 | NEXTDC S7 Sydney (OpenAI AI Campus) | NEXTDC | nextdc | NEXTDC (ASX: NXT) | NSW | Eastern Creek, Sydney | South of Honeycomb Drive / east of future Archbold Road, Eastern Creek NSW 2766 | -33.7872 | 150.8405 | Planning | Hyperscale | 2024 |  |  | 612 | 25.5 | 7000 | OpenAI (MOU Dec 2025, foundational customer) | Master plan of nine buildings across three blocks plus on-site substation; Sydney West bulk supply. Recycled-water cooling dropped after pipeline permit refused, switched to waterless coolant. Phase 1 targeted mid-2027; EIS under preparation, IDA-endorsed Mar 2026. | liquid (waterless) |  | NEXTDC's ~$7bn, 612MW AI campus on a $353m Eastern Creek land parcel, positioned as OpenAI's Australian 'Stargate' anchor under a December 2025 MOU. | NEXTDC以3.53亿澳元购入Eastern Creek地块后规划的约70亿澳元、612 MW AI园区，依托2025年12月与OpenAI签署的MOU，定位为OpenAI在澳洲的"Stargate"锁定项目。 | https://www.datacenterdynamics.com/en/news/australian-stargate-data-center-in-sydney-will-offer-612mw-of-capacity/ ¦ https://www.nextdc.com/data-centres/sydney-data-centres/s7-sydney ¦ https://www.pittwateronlinenews.com/NSW-Data-Centres-Framework-Released-Aug2026.php | 2026-09-15 | IT load
stack-syd01-erskine-park | STACK Infrastructure SYD01 Erskine Park | STACK Infrastructure | stack-infrastructure | STACK Infrastructure (IPI Partners / Blue Owl); site ex-ESR Logos | NSW | Erskine Park, Sydney | 78 Lockwood Road, Erskine Park NSW 2759 | -33.8102 | 150.7962 | Planning | Hyperscale | 2025 |  |  | 450 | 7.7 | 3700 | Undisclosed hyperscalers | Endeavour/Transgrid Erskine Park supply; 156 backup generators; three-storey 82,020 sqm building. SEARS Apr 2025, EIS exhibited (EDC ~$3.7bn per exhibition; initial filing cited $650m), IDA-endorsed Mar 2026. | liquid-ready |  | STACK's entry into Sydney: a 450MW single-building hyperscale campus at Erskine Park, exhibited in 2025-26 and fast-tracked through the NSW IDA pipeline. | STACK进入悉尼市场的首个项目：Erskine Park的450 MW单体超大规模园区，2025–26年公示，并纳入新州IDA加速通道。 | https://www.datacenterdynamics.com/en/news/stack-files-for-450mw-data-center-campus-in-sydney-australia/ ¦ https://urbandigest.com.au/3-7bn-erskine-park-data-centre-hits-public-exhibition/ ¦ https://www.stackinfra.com/locations/asia-pacific/sydney/syd01/ | 2026-09-15 | IT load
stockland-fife-kemps-creek | Stockland / Fife Capital Kemps Creek Data Centre (90 Aldington Road) | Stockland / Fife Capital | stockland | Stockland (ASX: SGP) / Fife Capital JV | NSW | Kemps Creek, Sydney | 90 Aldington Road, Kemps Creek NSW 2178 | -33.8742 | 150.7802 | Planning | Hyperscale | 2025 |  |  | 168 | 9.24 | 3940 | Undisclosed | Served by planned 1GW substation for the Aldington Road industrial estate (Transgrid/Endeavour); twelve 14MW halls; direct-to-chip liquid cooling support. SEARS 2025; IDA-endorsed Mar 2026. | liquid (direct-to-chip) |  | A ~$3.9bn, 168MW liquid-cooled data centre proposed by Stockland and Fife Capital within the Aldington Road estate in the Mamre Road precinct. | Stockland与Fife Capital在Mamre Road片区Aldington Road产业园内提出的168 MW液冷数据中心，投资约39亿澳元，目前处于规划阶段。 | https://www.datacenterdynamics.com/en/news/stockland-files-to-build-168mw-data-center-in-sydney-australia/ ¦ https://www.planningportal.nsw.gov.au/major-projects/projects/90-aldington-road-data-centre | 2026-09-15 | IT load
stockland-davis-rd-wetherill-park | Stockland Davis Road Wetherill Park (Project Blue Tongue) | Stockland / EdgeConneX | stockland | Stockland (ASX: SGP) / EdgeConneX 50:50 JV | NSW | Wetherill Park, Sydney | 2-3 Davis Road, Wetherill Park NSW 2164 | -33.8482 | 150.8992 | Planning | Hyperscale | 2024 |  |  | 160 | 4.46 |  | Undisclosed hyperscaler | Dedicated Transgrid substation on site; two 80MW buildings (66MW IT each) plus tape vault; direct evaporative cooling with outside-air economisation. SSD exhibited 2024, IDA-endorsed Mar 2026; ITK cites 2027 target. | direct evaporative / free-air |  | A 160MW two-building campus with a hyperscaler-style tape archive on Stockland's Wetherill Park logistics site, now progressed with EdgeConneX as JV partner. | Stockland在Wetherill Park物流用地上规划的160 MW双楼园区，附带超大规模客户所需的磁带归档库，现由Stockland与EdgeConneX合资推进。 | https://www.datacenterdynamics.com/en/news/160mw-data-center-campus-and-tape-building-proposed-in-sydney-australia/ ¦ https://itkservices3.com/background/data_centres_australia_top10_construction ¦ https://w.media/stockland-finalises-edgeconnex-data-centre-jv-as-ceo-plots-more-investment/ | 2026-09-15 | IT load
stockland-mpark-stage2 | Stockland MPark Stage 2 Data Centre (Project A) | Stockland / EdgeConneX | stockland | Stockland (ASX: SGP) / EdgeConneX JV | NSW | Macquarie Park, Sydney | 1-5 Khartoum Road, Macquarie Park NSW 2113 | -33.7782 | 151.1202 | Approved | Hyperscale | 2024 |  |  | 100 |  |  | Undisclosed (MPark Stage 1 DC leased to hyperscaler) | Ausgrid Macquarie Park network; 100MW+ secured per Stockland; six-storey building replacing car park; SSD approved 2026. |  |  | The second data centre at Stockland's MPark technology precinct, an approved six-storey 100MW+ building being delivered through the Stockland-EdgeConneX joint venture. | Stockland MPark科技园区的第二座数据中心，六层、100 MW以上，已获批，由Stockland与EdgeConneX合资交付。 | https://www.telecompaper.com/news/nsw-approves-stockland-hyperscale-data-centre-for-sydney--1564864 ¦ https://w.media/stockland-finalises-edgeconnex-data-centre-jv-as-ceo-plots-more-investment/ | 2026-09-15 | IT load
akaysha-muswellbrook | Upper Hunter Data Centre & 2GW Battery (Akaysha Energy consortium) | Akaysha Energy consortium (proponent) |  | Akaysha Energy (BlackRock) consortium; land: Malabar Resources | NSW | Between Denman and Muswellbrook, Upper Hunter | Malabar Resources land, Denman-Muswellbrook, NSW 2333 | -32.3302 | 150.8002 | Planning | Hyperscale | 2026 |  |  | 1000 |  | 10000 | Reported targets: Google, Microsoft (unconfirmed) | Co-located 2,000MW battery drawing on 500kV Bayswater and Sandy Creek Road substations carrying Central-West Orana / New England REZ output; scoping report to DPHI mid-2026; 2-3 year build. |  |  | A $10bn proposal pairing a ~1GW data centre with Australia's largest (2GW) battery on mining land in the Upper Hunter, positioned to absorb renewable-zone output near Bayswater. | Akaysha Energy牵头在Upper Hunter矿业用地上提出的100亿澳元项目，将约1 GW数据中心与澳洲最大的2 GW电池配套，就近消纳Bayswater周边可再生能源区的出力。 | https://www.newcastleherald.com.au/story/9277341/10-billion-battery-and-data-centre-proposed-for-muswellbrook/ ¦ https://www.newcastleherald.com.au/story/9331916/hunter-region-data-centres-to-drive-wind-energy-diversify-economy/ | 2026-09-15 | Site generation
beetaloo-digital-weddell | Beetaloo Digital Weddell Hyperscale Campus | Beetaloo Digital |  | Beetaloo Energy (ASX: BTL) | NT | Weddell, ~30km south of Darwin | Weddell NT 0822 | -12.63 | 131 | Planning | Hyperscale | 2026 |  | 0 | 2000 | 185 | 40000 | Undisclosed hyperscalers (up to two campuses) | Up to 2GW on-site gas-fired generation fuelled by Beetaloo Basin gas; NT Government granted 12-month exclusive commitment over 185ha site (Jul 2026); Halliburton MoU on upstream; strong environmental criticism |  |  | Beetaloo Energy's proposed A$40bn, 2GW gas-powered hyperscale precinct at Weddell south of Darwin, backed by a 12-month NT Government exclusivity over 185ha and the largest data centre proposal in northern Australia. | Beetaloo Energy拟在达尔文以南Weddell建设的2 GW燃气供电超大规模园区，投资400亿澳元；北领地政府已就185公顷用地授予12个月独家开发权，是澳洲北部规模最大的数据中心提案。 | https://territorycoordinator.nt.gov.au/news-and-insights/beetaloo-digital-advances-plans-for-weddell-data-centre ¦ https://www.abc.net.au/news/2026-07-22/beetaloo-digital-energy-ai-hyperscale-data-centre-40-billion/106943690 | 2026-09-15 | Site generation
energy-north-project-ares | Energy North Project Ares (Murranji Station) | Energy North |  | Energy North | NT | Murranji Station, Barkly Region | Murranji Station, Barkly Region NT | -17 | 132.3 | Planning | Hyperscale | 2026 |  | 0 | 1000 | 19150 |  | Undisclosed | Fully off-grid hybrid gas and 6,000-7,000ha solar; ~90ha of data halls; up to 4GL/yr groundwater; referred to federal environment regulator (EPBC), public comment 2026 |  |  | Perth-based Energy North's 1GW off-grid hyperscale proposal on 19,150ha at Murranji Station in the NT outback, combining gas and solar generation with its own airstrip and rail link, now in federal environmental assessment. | 珀斯企业Energy North拟在北领地内陆Murranji Station 19,150公顷土地上开发的1 GW离网超大规模项目，燃气加光伏混合供电，自建机场跑道和铁路连接，目前正接受联邦环评。 | https://www.abc.net.au/news/2026-07-01/data-centre-planned-outback-nt/106862398 | 2026-09-15 | Site generation
inligo-darwin-cls | Inligo Darwin Cable Landing Station & Data Centre | Inligo Digital Australia |  | Inligo Networks | NT | Fannie Bay, Darwin | Near Fannie Bay, Darwin NT 0820 | -12.426 | 130.839 | Under Construction | Edge | 2023 |  | 0 |  |  |  | Asia Connect Cable (ACC-1), Unite domestic cable, carriers | Purpose-built landing station for up to four international subsea cables (ACC-1 first) plus colocation; completion targeted 2026 | air |  | Inligo's purpose-built Darwin cable landing station and edge data centre near Fannie Bay, designed to terminate up to four subsea systems including the Asia Connect Cable to Singapore and the US, positioning Darwin as a northern digital gateway. | Inligo在达尔文Fannie Bay附近在建的专用海缆登陆站兼边缘数据中心，可终接最多四条国际海缆（首条为通往新加坡和美国的Asia Connect Cable），目标将达尔文建成澳洲北部的数字门户。 | https://www.inligonetworks.com/darwin-cable-landing-station/ ¦ https://www.datacenterdynamics.com/en/news/inligo-networks-begins-construction-of-darwin-cable-landing-station/ | 2026-09-15 | IT load
nextdc-d1 | NEXTDC D1 Darwin | NEXTDC | nextdc | NEXTDC | NT | Darwin CBD | Darwin CBD NT 0800 | -12.463 | 130.842 | Operational | Colocation | 2022 | 2024 | 1 | 7 |  | 80 | NT Government, Vocus, Aussie Broadband, GSL Networks, NetVault | Integrated with Vocus Terabit Territory fibre and the Darwin-Jakarta-Singapore Cable landing; 7MW target capacity, initial phase live Aug 2024 | air | Target Uptime Tier III, ISO 27001 | NEXTDC's A$80m D1 Darwin, opened August 2024 with NT Government and Vocus, is the Territory's first carrier-neutral colocation facility and the interconnection point for the Darwin-Jakarta-Singapore subsea cable. | NEXTDC投资8,000万澳元的达尔文D1，2024年8月携北领地政府和Vocus开业，是北领地首座运营商中立托管设施，也是达尔文—雅加达—新加坡海缆的互联节点；规划7 MW，首期1 MW在运。 | https://www.nextdc.com/news/nextdc-opens-80m-data-centre-in-darwin-with-nt-gov-and-vocus-in-major-boost-to-the-regions-growing-digital-economy ¦ https://www.nextdc.com/data-centres/darwin-data-centres/d1-darwin | 2026-09-15 | IT load
digico-brisbane-airport | DigiCo Brisbane Airport Campus (BNE1/BNE2/BNE3, ex-iseek) | DigiCo Infrastructure REIT | digico | DigiCo Infrastructure REIT (HMC Capital) | QLD | Eagle Farm (Brisbane Airport), Brisbane | 2-6 Cycas Lane, Brisbane Airport QLD 4008 | -27.403 | 153.093 | Operational | Colocation | 2013 | 2014 |  |  |  |  | Queensland enterprise, government, cloud | Multi-building campus grown from iseek's 4MW Eagle Farm facility with 6MW Tier IV-rated expansion (2019); acquired by DigiCo REIT in 2024 | air | Uptime Tier IV (BNE2 claimed), ISO 27001 | The former iseek Brisbane Airport campus, now DigiCo BNE1-3, a multi-building Tier IV-rated colocation site at Eagle Farm that is one of Brisbane's larger independent facilities. | 原iseek布里斯班机场园区，现为DigiCo BNE1–3，位于Eagle Farm，多栋楼、Tier IV级别，是布里斯班规模较大的独立托管设施之一。 | https://www.datacenterdynamics.com/en/news/iseek-double-power-capacity-brisbane-campus/ ¦ https://www.datacentermap.com/australia/brisbane/ | 2026-09-15 | IT load
interactive-brisbane | Interactive Brisbane Eight Mile Plains | Interactive | interactive | Interactive Pty Ltd | QLD | Eight Mile Plains, Brisbane | 19 McKechnie Drive, Eight Mile Plains QLD 4113 | -27.585 | 153.093 | Operational | Colocation | [6 empty] | Enterprise, government | Brisbane Technology Park colocation site | air | ISO 27001 | Interactive's Brisbane colocation and managed services facility in the Eight Mile Plains technology park, part of the southern Brisbane enterprise data centre cluster alongside Fujitsu and Host Networks. | Interactive在布里斯班Eight Mile Plains科技园的托管与管理服务设施，与Fujitsu、Host Networks共同构成布里斯班南部的企业数据中心集群。 | https://baxtel.com/data-center/interactive-brisbane ¦ https://www.datacentermap.com/australia/brisbane/ | 2026-09-15 | IT load
nextdc-b1 | NEXTDC B1 Brisbane | NEXTDC | nextdc | NEXTDC | QLD | Brisbane CBD | 20 Wharf Street, Brisbane QLD 4000 | -27.465 | 153.029 | Operational | Colocation | 2010 | 2011 | 2.25 | 2.25 |  |  | Enterprise, carriers | CBD interconnection site | air | Uptime Tier III, ISO 27001 | NEXTDC's first-ever facility (2011), a 2.25MW CBD interconnection site that remains a key Brisbane carrier hub. | NEXTDC的首座数据中心（2011年），位于布里斯班CBD，IT负载2.25 MW，至今仍是布里斯班重要的运营商互联节点。 | https://www.nextdc.com/data-centres ¦ https://www.datacentermap.com/australia/brisbane/ | 2026-09-15 | IT load
nextdc-b2 | NEXTDC B2 Fortitude Valley | NEXTDC | nextdc | NEXTDC | QLD | Fortitude Valley, Brisbane | 454 St Pauls Terrace, Fortitude Valley QLD 4006 | -27.454 | 153.033 | Operational | Colocation | 2015 | 2017 | 12 | 12 |  |  | Queensland Government, enterprise, cloud on-ramps | Dual Energex feeds; 12MW IT design | air | Uptime Tier IV Certified Constructed Facility, Tier IV Gold Operational Sustainability, ISO 27001 | NEXTDC's Tier IV Brisbane flagship in Fortitude Valley, a 12MW carrier-dense colocation facility serving Queensland Government and enterprise cloud connectivity. | NEXTDC在布里斯班Fortitude Valley的Tier IV旗舰，IT负载12 MW，2017年投运，运营商密度高，服务昆州政府和企业云互联需求。 | https://www.nextdc.com/data-centres ¦ https://www.datacentermap.com/australia/brisbane/ | 2026-09-15 | IT load
nextdc-gc1 | NEXTDC GC1 Gold Coast | NEXTDC | nextdc | NEXTDC | QLD | Southport, Gold Coast | Southport QLD 4215 | -27.967 | 153.4 | Planning | Edge | 2024 |  | 0 | 6 |  |  | Regional enterprise, government, health | 6MW regional edge design | air | Target Uptime Tier III | NEXTDC's planned 6MW Gold Coast edge facility in Southport, the first purpose-built colocation data centre for Australia's sixth-largest city. | NEXTDC规划中的Gold Coast边缘设施，位于Southport，6 MW，将是澳洲第六大城市首座专建托管数据中心。 | https://www.nextdc.com/data-centres/gold-coast-data-centres/gc1-gold-coast | 2026-09-15 | IT load
nextdc-sc2 | NEXTDC SC2 Sunshine Coast | NEXTDC | nextdc | NEXTDC | QLD | Maroochydore, Sunshine Coast | Maroochydore QLD 4558 | -26.65 | 153.09 | Under Construction | Edge | 2024 |  | 0 | 6 |  |  | Regional enterprise, subsea cable users | Adjacent to JGA-South subsea cable landing at Maroochydore; 6MW design | air | Target Uptime Tier III | NEXTDC's 6MW second Sunshine Coast facility under development near the Maroochydore international subsea cable landing station, complementing the 1MW SC1. | NEXTDC在Sunshine Coast的第二座设施，位于Maroochydore国际海缆登陆站附近，规划6 MW，目前在建，与1 MW的SC1互补。 | https://www.nextdc.com/data-centres/sunshine-coast-data-centres/sc2-sunshine-coast ¦ https://renewmap.com.au/resources/projects/qld/datacentre/ | 2026-09-15 | IT load
polaris-springfield | Polaris Data Centre Springfield | Polaris | polaris | Springfield City Group (Springfield Land Corporation) | QLD | Springfield Central, Greater Springfield | 11 Mary Mackenroth Lane, Springfield Central QLD 4300 | -27.666 | 152.91 | Operational | Colocation | 2007 | 2008 |  |  |  |  | Queensland Government, enterprise, Oper8 | Purpose-built 2008 facility in Greater Springfield master-planned city; capacity not publicly disclosed | air | Uptime Tier III (design) | Queensland's first purpose-built commercial Tier III data centre (2008) in the Greater Springfield master-planned city, home to government and enterprise tenants and the Oper8 colocation operation. | 昆州首座专建商业Tier III数据中心，2008年投运，位于Greater Springfield规划新城，租户包括昆州政府、企业及Oper8托管业务；容量未公开。 | https://www.polarisdatacentre.com.au/ ¦ https://baxtel.com/data-center/polaris-brisbane | 2026-09-15 | IT load
quinbrook-supernode | Quinbrook Supernode Brendale | Quinbrook Infrastructure Partners |  | Quinbrook Infrastructure Partners | QLD | Brendale, Moreton Bay (north Brisbane) | 83 Kremzow Road, Brendale QLD 4500 | -27.317 | 152.982 | Approved | Hyperscale | 2022 |  | 0 | 800 | 30 | 2500 | Undisclosed hyperscalers (multi-tenant, up to four campuses) | Three HV connections to adjacent Powerlink South Pine substation; up to 800MW; up to 2,000MWh co-located BESS (Supernode battery stage 1 operating); FIRB and Moreton Bay planning approvals obtained | liquid-ready |  | Quinbrook's 30ha Supernode precinct next to the South Pine substation in Brendale, approved for up to four hyperscale data centres totalling 800MW alongside a multi-GWh grid battery already in operation. | Quinbrook在Brendale South Pine变电站旁开发的30公顷Supernode园区，已获批建设最多四座超大规模数据中心、合计800 MW，配套的数GWh电网储能一期已投运。 | https://qcn.com.au/commsday-quinbrook-plans-2-5bn-dc-campus-in-north-brisbane-with-800mw-of-renewable-power/ ¦ https://renewmap.com.au/resources/projects/qld/datacentre/ | 2026-09-15 | IT load
swanbank-ipswich | Swanbank Data Centre (Northern Concept) | Northern Concept Swanb Pty Ltd |  | Northern Concept Swanb Pty Ltd | QLD | Swanbank, Ipswich | Lot 5 Six Leaf Street (formerly Patrick Street), Swanbank QLD 4306 | -27.656 | 152.82 | Planning | Hyperscale | 2026 |  | 0 |  | 8 |  | Undisclosed | Near Powerlink Blackstone substation, a planned 200MW BESS and Swanbank E gas power station; two stages totalling ~180,000 sqm GFA; recommended for approval by Ipswich council staff |  |  | A ten-storey, two-stage hyperscale data centre proposed on 8ha in the Swanbank industrial precinct at Ipswich, next to the Blackstone substation, which would be Queensland's tallest data centre. | 拟在Ipswich Swanbank工业区8公顷地块上建设的十层、两期超大规模数据中心，紧邻Powerlink Blackstone变电站，建成后将是昆州最高的数据中心建筑；容量未公开。 | https://www.datacenterdynamics.com/en/news/plans-filed-for-10-story-data-center-outside-brisbane-australia/ ¦ https://www.theurbandeveloper.com/articles/swanbank-data-centre-proposal-ipswich-tallest-building-qld | 2026-09-15 | IT load
zerra-western-downs | Zerra DC Western Downs Digital Park | Zerra DC |  | Consortium: Zerra DC / Australian Data Centres (85% Dexus-owned) / Macquarie Capital | QLD | Dalby / Kogan, Western Downs | 1933 Dalby-Kogan Road, Western Downs QLD 4405 | -27.05 | 150.99 | Planning | Hyperscale | 2026 |  | 0 | 2160 | 725.5 | 31900 | Anthropic (Australian subsidiary) - initial phase | 540MVA substation with direct high-voltage connection into the Braemar generation precinct; battery-backed power conditioning. Initially coal- and gas-fired supply until new renewable generation is built. Air cooling with closed-loop liquid supplement, rainwater harvesting and treated wastewater reuse. | air |  | On 16 September 2026 a consortium of Zerra DC, Australian Data Centres (85% owned by Dexus) and Macquarie Capital signed lease documentation with an Australian subsidiary of Anthropic for the initial phase of the Western Downs Digital Park at 1933 Dalby-Kogan Road — Australia's largest data centre lease to date. The 725ha campus is planned as four buildings of about 36,000sqm each with a 540MVA substation and roughly A$32 billion of investment over a four-to-six-year staged build. The development application lodged with Western Downs Regional Council on 17 August 2026 is still pending, and FIRB approval and a Dexus board decision remain outstanding. | 2026 年 9 月 16 日，Zerra DC、Australian Data Centres（Dexus 持股 85%）与 Macquarie Capital 组成的联合体，与 Anthropic 澳洲子公司签署租约文件，锁定 Western Downs Digital Park 首期算力，为澳洲迄今最大的数据中心租赁交易。园区位于 1933 Dalby-Kogan Road、占地 725 公顷，规划四栋各约 36,000 ㎡ 的机房，配 540 MVA 变电站，总投资约 319亿澳元，分期建设 4–6 年，Anthropic 目标 2027 年首次使用。开发申请已于 2026 年 8 月 17 日报 Western Downs Regional Council，仍待批；FIRB 审查与 Dexus 董事会批准亦为先决条件。初期供电依托 Braemar 一带的煤电与气电，可再生电源需后续建设，已引发政治争议。媒体对满建容量存在 1.44 GW 与 2.16 GW 两种口径。 | https://www.abc.net.au/news/2026-09-14/western-downs-digital-park-data-centre-energy-queensland/107115082 ¦ https://www.realestatesource.com.au/zerra-files-plans-for-31bn-queensland-data-centre-campus/ ¦ https://w.media/zerra-plans-1-44gw-aud-14-5bn-data-centre-campus-in-queensland/ | 2026-10-07 | Site/grid power
aurora-energy-precinct-dc | Aurora Energy Precinct AI Data Centre (1414 Degrees) | Undisclosed data centre developer |  | 1414 Degrees (precinct owner) / undisclosed developer | SA | Aurora, near Port Augusta SA | Aurora Energy Precinct, Carriewerloo Station, north of Port Augusta SA 5700 | -32.25 | 137.85 | Planning | Hyperscale | 2026 |  | 0 | 1000 | 40 |  | Undisclosed | Non-binding HoA (Aug 2026): 17MW phase 1 via 33kV, 200MW anchor campus via 275kV connection, scalable to 1GW; precinct has approved 140MW/280MWh BESS and up to 900MW solar potential |  |  | A phased AI campus (17MW, then 200MW, scaling to 1GW) proposed by an undisclosed developer on 40ha of 1414 Degrees' 1,580ha Aurora Energy Precinct near Port Augusta, the former solar-thermal site, under a non-binding August 2026 agreement. | 一家未披露的开发商拟在1414 Degrees位于Port Augusta附近的Aurora Energy Precinct（1,580公顷，原光热电站选址）内40公顷地块上分期建设AI园区，17 MW起步、再到200 MW、最终1 GW，2026年8月签署非约束性HoA。 | https://www.datacenterdynamics.com/en/news/1414-degrees-signs-deal-for-up-to-1gw-ai-campus-at-aurora-energy-precinct-in-south-australia/ ¦ https://reneweconomy.com.au/thermal-battery-company-chasing-1-gw-data-centre-deal-for-site-once-earmarked-for-giant-solar-towers/ | 2026-09-15 | Site generation
dci-adelaide-kidman-park | DCI Adelaide ADL01/ADL02 Kidman Park | DCI Data Centers | dci-data-centers | Brookfield / DCI Data Centers | SA | Kidman Park, Adelaide | 340 Findon Road, Kidman Park SA 5025 | -34.904 | 138.538 | Operational | Colocation | 2019 | 2021 |  | 10 |  |  | Australian Government, hyperscale cloud edge, enterprise | ADL02 10MW facility on the Kidman Park campus; sovereign-grade | air | Hosting Certification Framework Certified Strategic, Uptime Tier III, ISO 27001 | DCI's Adelaide campus at Kidman Park, including the 10MW ADL02 certified-strategic facility serving government and hyperscale edge demand in South Australia. | DCI在阿德莱德Kidman Park的园区，含10 MW的ADL02 Certified Strategic主权级设施，2021年投运，服务南澳政府和超大规模云边缘需求。 | https://baxtel.com/data-center/dci-adelaide ¦ https://renewmap.com.au/resources/projects/sa/datacentre/ | 2026-09-15 | IT load
digico-adl1-edinburgh-parks | DigiCo ADL1 Edinburgh Parks (ex-YourDC) | DigiCo Infrastructure REIT | digico | DigiCo Infrastructure REIT (HMC Capital) | SA | Edinburgh Parks, Adelaide | 23 Woomera Avenue, Edinburgh SA 5111 | -34.732 | 138.63 | Operational | Colocation | 2015 | 2016 |  | 15 |  | 30 | Defence industry, SA Government, enterprise | Adjacent to RAAF Base Edinburgh defence precinct; Tier III design; 15MW campus design | air | Uptime Tier III Certified Design, ISO 27001, DISP | The former YourDC Edinburgh Parks Tier III facility (opened 2016, A$30m), now DigiCo ADL1, serving Adelaide's defence-industry precinct next to RAAF Base Edinburgh with a 15MW campus design. | 原YourDC的Edinburgh Parks Tier III设施，2016年开业、投资3,000万澳元，现为DigiCo ADL1；紧邻RAAF Base Edinburgh防务产业区，园区设计容量15 MW。 | https://www.itnews.com.au/news/yourdc-opens-30m-tier-three-adelaide-data-centre-420056 ¦ https://www.datacentermap.com/australia/adelaide/yourdc-edinburgh/ | 2026-09-15 | IT load
firmus-tailem-bend | Firmus Tailem Bend AI Factory | Firmus Technologies | firmus | Firmus Technologies | SA | Tailem Bend, Murraylands SA | Farmland ~5km from Tailem Bend SA 5260 | -35.25 | 139.46 | Planning | Hyperscale | 2026 |  | 0 | 600 |  |  | Firmus / Sustainable Metal Cloud GPU cloud, NVIDIA-partner AI workloads | 600MW firm energy supply agreement with Gunvor (Jul 2026) linked to ~1.2GW new renewables and 1.5GWh BESS (12-year); plans not yet lodged; approval pathway being settled with SA Government | liquid-ready |  | Firmus's flagship South Australian AI factory near Tailem Bend, underpinned by a 600MW Gunvor energy supply deal tied to 1.2GW of new renewables and 1.5GWh of batteries, and being fast-tracked as Tasmanian approvals slow. | Firmus在南澳Tailem Bend附近规划的600 MW旗舰AI工厂，依托与Gunvor签订的600 MW供电协议（配套1.2 GW新建可再生能源和1.5 GWh储能），在塔州审批放缓之际正被加速推进。 | https://www.datacenterdynamics.com/en/news/firmus-signs-600mw-energy-supply-agreement-in-south-australia/ ¦ https://www.abc.net.au/news/2026-07-16/sa-firmus-factory-tailem-bend-community-meeting/106919542 ¦ https://firmus.co/newsroom/firmus-secures-600-mw-energy-supply-agreement-in-south-australia-linked-to-1-2-gw-of-new-renewable-generation-and-battery-storage | 2026-09-15 | IT load
iren-bundey | IREN Bundey AI Data Centre Campus | IREN |  | IREN Limited | SA | Bundey, Mid North SA | Sutherlands Road & Powerline Road, Bundey SA 5320 | -34.03 | 139.3 | Planning | Hyperscale | 2026 |  | 0 | 800 |  | 10000 | AI cloud (IREN own GPU cloud and hyperscale customers) | Transmission connection agreement at ElectraNet Bundey 275kV hub (Robertstown/Bundey node of Project EnergyConnect); energisation targeted 2028; closed-loop liquid cooling; development application not yet lodged | liquid-ready |  | IREN's first Australian campus, an 800MW, ~A$10bn AI data centre at the Bundey transmission hub 125km north-east of Adelaide with energisation targeted for 2028, announced June 2026 amid local water-use concerns. | IREN在澳洲的首个园区，位于阿德莱德东北125 km的Bundey输电枢纽，规划800 MW、投资约100亿澳元，目标2028年送电；2026年6月宣布后引发当地对用水问题的关注。 | https://www.datacenterdynamics.com/en/news/iren-targets-australia-for-800mw-data-center-campus/ ¦ https://iren.gcs-web.com/news-releases/news-release-details/iren-announces-first-australian-data-center-campus-800mw-south ¦ https://www.abc.net.au/news/2026-06-19/proposed-data-centre-in-south-australia-dividing-locals/106810776 | 2026-09-15 | IT load
nextdc-a1 | NEXTDC A1 Adelaide | NEXTDC | nextdc | NEXTDC | SA | Adelaide CBD | 125 Frome Street, Adelaide SA 5000 | -34.927 | 138.608 | Operational | Colocation | 2013 | 2015 | 5 | 5 |  |  | SA Government, enterprise, cloud on-ramps | CBD site; 5MW IT design | air | Uptime Tier III Certified, ISO 27001 | NEXTDC's 5MW Adelaide CBD colocation facility, the city's principal carrier-neutral interconnection point. | NEXTDC在阿德莱德CBD的5 MW托管设施，2015年投运，是该市主要的运营商中立互联节点。 | https://www.nextdc.com/data-centres ¦ https://renewmap.com.au/resources/projects/sa/datacentre/ | 2026-09-15 | IT load
firmus-bell-bay | Firmus Project Southgate Bell Bay (Long Reach) | Firmus Technologies | firmus | Firmus Technologies | TAS | Bell Bay / Long Reach, George Town | Lot 1 East Tamar Highway, Long Reach TAS 7253 (former Gunns pulp mill site) | -41.14 | 146.89 | Approved | Hyperscale | 2026 |  | 0 | 288 |  |  | Firmus / Sustainable Metal Cloud GPU cloud | Hydro Tasmania disclosed on 28 September 2026 that it is assessing supply for ~444MW of combined Firmus demand across Bell Bay, St Leonards and Wesley Vale, under two contracting models: Firmus contracting directly with renewable generators and Hydro firming, or Firmus contracting with Hydro which procures new generation. Firmus has sought 2MW of new renewable capacity for every 1MW of load. No decision made; assessment due to conclude end-2026. Planning consents and TasNetworks connection arrangements to be negotiated separately. | liquid-ready |  | Firmus's 288MW AI factory on the former Gunns pulp mill site at Bell Bay, approved by George Town Council in August 2026 amid strong local opposition, with Firmus now appealing generator-use conditions. | Firmus在Bell Bay原Gunns纸浆厂地块上的288 MW AI工厂，2026年8月在强烈社区反对下获George Town Council批准，公司目前正就发电机运行限制条件提起上诉。 | https://www.abc.net.au/news/2026-08-25/firmus-ai-bell-bay-receives-george-town-council-approval/107074336 ¦ https://www.abc.net.au/news/2026-09-15/firmus-technologies-lodge-tascat-appeal-for-generator-use/107144572 ¦ https://firmus.co/project-southgate-faqs | 2026-10-07 | IT load
firmus-southgate-st-leonards | Firmus Project Southgate St Leonards (Launceston) | Firmus Technologies | firmus | Firmus Technologies | TAS | St Leonards, Launceston | St Leonards, Launceston TAS 7250 | -41.46 | 147.21 | Under Construction | Hyperscale | 2025 |  |  | 104 | 5 | 2100 | Firmus / Sustainable Metal Cloud GPU cloud, NVIDIA GB300-class AI | Covered by Hydro Tasmania's 28 September 2026 assessment of ~444MW of combined Firmus demand across St Leonards, Bell Bay and Wesley Vale; two contracting models under review and Firmus has sought 2MW of new renewable capacity per 1MW of load. No decision made; assessment due end-2026. TasNetworks connection to be negotiated separately. | liquid-ready |  | Firmus's flagship hydro-powered AI factory at St Leonards, approved by Launceston City Council in September 2025 (A$2.1bn stage 1) and under construction, with two server halls and a 300MW second stage planned. | Firmus在Launceston St Leonards的旗舰水电AI工厂，2025年9月获Launceston City Council批准（一期投资21亿澳元），目前在建，规划两座服务器大厅，约104 MW已获批，二期300 MW待审批。 | https://www.datacenterdynamics.com/en/news/firmus-gets-go-ahead-for-ai-data-center-project-in-launceston-tasmania/ ¦ https://firmus.co/newsroom/tasmanian-world-first-ai-factory-zone-clears-path-for-firmus-project-southgate ¦ https://www.abc.net.au/news/2026-08-25/firmus-ai-bell-bay-receives-george-town-council-approval/107074336 | 2026-10-07 | IT load
firmus-wesley-vale | Firmus Project Southgate Wesley Vale | Firmus Technologies | firmus | Firmus Technologies | TAS | Wesley Vale, north-west Tasmania | Wesley Vale TAS 7307 | -41.21 | 146.43 | Planning | Hyperscale | 2026 |  | 0 | 52 |  |  | Firmus / Sustainable Metal Cloud GPU cloud | Covered by Hydro Tasmania's 28 September 2026 assessment of ~444MW of combined Firmus demand across Wesley Vale, St Leonards and Bell Bay; two contracting models under review and Firmus has sought 2MW of new renewable capacity per 1MW of load. No decision made; assessment due end-2026. TasNetworks connection to be negotiated separately. | liquid-ready |  | The third and smallest Firmus Tasmanian site, a 52MW AI facility proposed at Wesley Vale in the north-west, with a development application lodged in 2026. | Firmus在塔州的第三个、也是最小的站点，拟在西北部Wesley Vale建设52 MW AI设施，开发申请已于2026年递交。 | https://www.abc.net.au/news/2026-08-25/firmus-ai-bell-bay-receives-george-town-council-approval/107074336 ¦ https://www.abc.net.au/news/2026-07-03/firmus-ai-data-centres-is-tasmania-ready/106869862 | 2026-10-07 | IT load
aws-cobblebank | AWS Cobblebank (Ferris Road) Data Centre | AWS | aws | Amazon | VIC | Cobblebank (Melton), Melbourne | 54-80 Ferris Road, Cobblebank VIC 3338 | -37.717 | 144.607 | Approved | Hyperscale campus (self-build) | 2024 |  |  | 40 | 13.2 |  | AWS (Asia Pacific Melbourne Region) | 13.2ha site bought for A$60.5m (Jul 2023); 40MW facility; part of A$6.8bn AWS Melbourne Region investment |  |  | AWS's self-build 40MW data centre on 13.2ha at Cobblebank in the Melton growth corridor, expanding the AWS Asia Pacific (Melbourne) Region launched in 2023. | AWS在Melton增长走廊Cobblebank 13.2公顷地块上自建的40 MW数据中心，已获批，用于扩展2023年上线的AWS亚太（墨尔本）区域。 | https://www.theurbandeveloper.com/articles/amazon-plans-more-data-centres-in-sydney-and-melbourne ¦ https://baxtel.com/data-center/amazon-ferris-road | 2026-09-15 | IT load
aws-mickleham | AWS Mickleham (Donnybrook Road) Data Centre | AWS | aws | Amazon | VIC | Mickleham, Melbourne | 55 Donnybrook Road, Mickleham VIC 3064 | -37.536 | 144.917 | Planning | Hyperscale campus (self-build) | 2024 | [5 empty] | AWS (Asia Pacific Melbourne Region) | Northern Melbourne self-build site; capacity not disclosed VIC ministerial permit PA2604506 (45 Donnybrook Road, Mickleham; seven data centre parcels, Buildings A-G) received 1 Jul 2026, at referral. |  |  | AWS's northern Melbourne self-build site on Donnybrook Road, Mickleham, one of several land holdings supporting the Asia Pacific (Melbourne) Region's A$6.8bn build-out. | AWS在墨尔本北部Mickleham Donnybrook Road的自建用地，是支撑亚太（墨尔本）区域68亿澳元扩建的多个地块之一；容量未公开，处于规划阶段。 | https://www.datacentermap.com/australia/melbourne/amazon-aws-55-donnybrook-rd/ ¦ https://w.media/amazons-investment-into-data-centres-in-australia-the-next-chapter/ | 2026-10-07 | IT load
aws-truganina | AWS Truganina (Delivery Drive) Data Centre | AWS | aws | Amazon | VIC | Truganina, Melbourne | 22 Delivery Drive, Truganina VIC 3029 | -37.818 | 144.726 | Operational | Hyperscale campus (self-build) | 2020 | 2023 |  |  |  |  | AWS (Asia Pacific Melbourne Region) | Western Melbourne self-build supporting the AWS Melbourne Region (launched Jan 2023) |  |  | AWS's self-built western Melbourne data centre in Truganina, part of the infrastructure behind the Asia Pacific (Melbourne) Region launched in January 2023. | AWS在墨尔本西部Truganina自建的数据中心，2023年投运，是2023年1月上线的亚太（墨尔本）区域的底层基础设施之一。 | https://www.datacentermap.com/australia/melbourne/ ¦ https://w.media/amazons-investment-into-data-centres-in-australia-the-next-chapter/ | 2026-09-15 | IT load
airtrunk-mel1 | AirTrunk MEL1 Derrimut | AirTrunk | airtrunk | Blackstone / CPP Investments (AirTrunk) | VIC | Derrimut, Melbourne | 176 Swann Drive, Derrimut VIC 3026 | -37.7995 | 144.7742 | Operational | Hyperscale | 2016 | 2017 | 185 | 276 | 8.8 |  | Undisclosed hyperscalers (Microsoft reported), Datacom | Diverse 66kV HV feeds; campus expanded to 185MW (2023) with further phases to 276MW+; AirTrunk 100% renewables target via PPAs | hybrid | ISO 27001, PCI DSS, ISAE 3402, SCEC Zone 3 | AirTrunk's first Melbourne hyperscale campus in the western Derrimut industrial precinct, live since 2017 and progressively expanded to 185MW with a 276MW+ full-build design. Anchors Melbourne's west as the state's primary hyperscale cluster. | AirTrunk在墨尔本的首个超大规模园区，位于西部Derrimut工业区，2017年投运，已分期扩容至185 MW，满建设计276 MW以上，是墨尔本西部超大规模集群的核心资产。 | https://airtrunk.com/airtrunk-expands-mel1-to-185mw-capacity/ ¦ https://baxtel.com/data-center/airtrunk-melbourne-mel1 ¦ https://renewmap.com.au/resources/projects/vic/datacentre/ | 2026-09-15 | IT load
airtrunk-mel2 | AirTrunk MEL2 Mickleham | AirTrunk | airtrunk | Blackstone / CPP Investments (AirTrunk) | VIC | Mickleham, Melbourne (north-west) | 45 Donnybrook Road, Mickleham VIC 3064 (reported; AirTrunk has not confirmed the exact address) | -37.5355 | 144.916 | Planning | Hyperscale | 2025 |  | 0 | 354 | 67 | 5000 | Undisclosed hyperscaler | Multi-phase build in Melbourne's north-west; first capacity targeted 2H 2027; seven parcels, 4-5 storey buildings under state-assessed planning application (Development Facilitation Program) | liquid-ready |  | AirTrunk's second Melbourne campus, announced December 2025 as a 354MW, A$5bn+ multi-phase hyperscale development lifting the operator's Melbourne footprint to 630MW+. Widely reported to be the 67ha Donnybrook Road, Mickleham land bought for ~A$350m, with a planning application filed mid-2026. | AirTrunk 2025年12月宣布的第二座墨尔本园区，规划354 MW、投资逾50亿澳元，建成后其墨尔本总容量将超过630 MW；据广泛报道选址为Mickleham Donnybrook Road约67公顷地块（购地约3.5亿澳元），规划申请2026年中提交，首期目标2027年下半年。 | https://airtrunk.com/airtrunk-expands-australian-platform-with-a-second-hyperscale-data-centre-campus-in-melbourne/ ¦ https://www.crn.com.au/news/2026/data-centre/airtrunk-new-melbourne-location-mel2 ¦ https://certifiedstrategic.com/insights/melbourne-data-centre-pipeline-four-new-campuses | 2026-09-15 | IT load
cdc-brooklyn | CDC Brooklyn Campus | CDC Data Centres | cdc | Infratil / Future Fund / CSC (CDC Data Centres) | VIC | Brooklyn, Melbourne | 594 Geelong Road, Brooklyn VIC 3012 | -37.814 | 144.837 | Operational | Hyperscale | 2021 | 2024 |  | 350 |  |  | Australian Government, Microsoft, AWS (reported), sovereign enterprise | Brooklyn Campus One (150-155MW) and Campus Two (200MW) both operating; third building in planning; 350MW+ at completion | hybrid | Hosting Certification Framework Certified Strategic, ISO 27001, DISP | CDC's inaugural Melbourne campus in Brooklyn, officially opened March 2026 with two operating buildings (Campus One and Two) and 350MW+ capacity at completion, serving sovereign government and hyperscale tenants. | CDC在墨尔本的首个园区，位于Brooklyn，2026年3月正式开业，Campus One和Campus Two两栋楼已投运，满建容量350 MW以上，服务主权政府和超大规模云租户。 | https://cdc.com/locations/melbourne/ ¦ https://invest.vic.gov.au/news-and-events/news/2026/march/cdc-data-centres-officially-opens-its-first-melbourne-campus,-expanding-its-ability-to-deliver-secure-and-sustainable-solutions ¦ https://renewmap.com.au/resources/projects/vic/datacentre/ | 2026-09-15 | IT load
cdc-laverton | CDC Laverton Campus | CDC Data Centres | cdc | Infratil / Future Fund / CSC (CDC Data Centres) | VIC | Laverton North, Melbourne | Leakes Road, Laverton North VIC 3026 | -37.827 | 144.775 | Under Construction | Hyperscale | 2024 |  | 0 | 400 |  | 2700 | Undisclosed hyperscaler / government | Ground broken 17 Feb 2025; Laverton Campus One (150MW) and Campus Two (300MW) under construction; 400MW+ additional regional capacity | hybrid | Target Hosting Certification Framework Certified Strategic | CDC's second Melbourne campus, a A$2.7bn, 400MW+ hyperscale development in Laverton North under construction since February 2025 that will lift CDC's Victorian capacity to 780MW+. | CDC的第二座墨尔本园区，位于Laverton North，投资27亿澳元、规划400 MW以上，2025年2月动工，建成后CDC在维州的总容量将超过780 MW。 | https://cdc.com/resources/news/cdc-brings-27bn-groundbreaking-opportunity-to-melbournes-south-west/ ¦ https://cdc.com/locations/melbourne/ ¦ https://itkservices3.com/background/data_centres_australia_top10_construction | 2026-09-15 | IT load
centuria-clayton | Centuria / Telstra Clayton Data Centre (1822 Dandenong Rd) | Telstra (tenant) / Centuria Industrial REIT | centuria-resetdata | Centuria Industrial REIT | VIC | Clayton, Melbourne (south-east) | 1822 Dandenong Road, Clayton VIC 3168 | -37.918 | 145.129 | Operational | Enterprise/Government | 2020 | 1990 | 12 | 40 |  |  | Telstra, Maincode (AI) | Existing ~12MW across two buildings leased to Telstra (30-year lease); Centuria progressing approvals and power for up to 40MW expansion after Telstra partially surrenders land (mid-2027) | air |  | Monash City Council refused Centuria's proposed 38MW, A$137 million data centre at 1816-1832 Dandenong Road, Clayton on 29 September 2026, overturning the planning officers' recommendation to approve. Councillors cited the scale of electricity demand, noise and heat rejection on nearby homes, and inconsistency with Victoria's Sustainable Data Centre Action Plan released a week earlier - the building would have sat about 80m from residences against a proposed 150m separation. A separate 40MW application on the same site remains pending and depends on Telstra decommissioning its existing infrastructure around mid-2027. | Monash City Council 于 2026 年 9 月 29 日否决 Centuria 在 1816-1832 Dandenong Road, Clayton 新建 38 MW 数据中心的申请（造价 1.37亿澳元），推翻规划官员的批准建议。否决理由集中在用电规模、噪声与排热对周边住宅的影响，以及与维州一周前发布的 Sustainable Data Centre Action Plan 不符——拟建位置距住宅约 80 m，低于新规提出的 150 m 退让要求。同一场地另有一宗 40 MW 申请仍在审，需待 Telstra 现有设施于 2027 年中前后退役。Centuria 是否就否决提请复审尚无定论。该消息目前仅见 W.Media 一家报道。 | https://www.datacenterdynamics.com/en/news/centuria-plans-40mw-data-center-in-melbourne-australia/ ¦ https://www.realestatesource.com.au/centuria-pays-telstra-416-7m-for-clayton-data-centre/ | 2026-10-07 | IT load
galileo-clyde-north | Clyde North Data Centre Campus (Galileo Group land) | Undisclosed |  | Galileo Group (landowner) | VIC | Clyde North, Melbourne (south-east) | 585 Berwick-Cranbourne Road, Clyde North VIC 3978 | -38.117 | 145.335 | Planning | Hyperscale | 2026 |  | 0 |  | 53.6 | 1120 | Undisclosed | First data centre application in City of Casey; Urban Growth Zone; further information requested May 2026; objections lodged |  |  | A A$1.12bn hyperscale campus proposed on 53.6ha at Clyde North in Melbourne's south-east growth corridor, the first such application in the City of Casey and a rare pipeline project outside the western cluster. | 拟在墨尔本东南增长走廊Clyde North 53.6公顷土地上开发的超大规模园区，投资11.2亿澳元，是City of Casey首个数据中心申请，也是西部集群之外少有的管线项目。 | https://www.datacenterdynamics.com/en/news/au11-billion-data-center-project-proposed-outside-melbourne-australia/ ¦ https://certifiedstrategic.com/insights/melbourne-data-centre-pipeline-four-new-campuses | 2026-09-15 | IT load
digital-realty-deer-park | Digital Realty Deer Park Campus (MEL10/MEL11/MEL12) | Digital Realty | digital-realty | Digital Realty | VIC | Deer Park, Melbourne | 54-98 Radnor Drive, Deer Park VIC 3023 | -37.769 | 144.774 | Operational | Colocation | 2009 | 2011 |  |  |  |  | Enterprise, cloud, carriers | Three-building connected campus in Melbourne's north-west industrial belt | air | ISO 27001, PCI DSS, SOC | Digital Realty's three-building connected colocation campus on Radnor Drive, Deer Park, serving enterprise and cloud interconnection in Melbourne's west. | Digital Realty在Deer Park Radnor Drive的三栋互联托管园区，2011年投运，服务墨尔本西部的企业和云互联需求。 | https://www.digitalrealty.com/data-centers/asia-pacific/melbourne/mel11 ¦ https://www.datacentermap.com/australia/melbourne/ | 2026-09-15 | IT load
doverdc-sm1a | DoverDC SM1A South Morang | DoverDC |  | DoverDC (with ASX-listed REIT stake) | VIC | South Morang, Melbourne | 525-535 McDonalds Road / 765 Plenty Road, South Morang VIC 3752 | -37.649 | 145.092 | Approved | Hyperscale | 2024 |  | 0 | 120 | 3.5 |  | Undisclosed | Adjacent to AusNet South Morang Terminal Station (SMTS); permit granted Sep 2024; construction expected late 2026/early 2027, launch 2028-29 |  |  | DoverDC's approved 120MW, three-storey facility beside the South Morang Terminal Station in Melbourne's north, with construction expected from late 2026 despite a 4,600-signature community petition. | DoverDC已获批的120 MW三层设施，紧邻墨尔本北部AusNet South Morang终端站，预计2026年底动工；当地反对请愿已征集逾4,600个签名。 | https://www.datacenterdynamics.com/en/news/application-filed-for-200mw-data-center-in-melbourne-australia/ ¦ https://www.doverdc.com.au/data-centre-sm1 | 2026-09-15 | IT load
doverdc-sm1b | DoverDC SM1B South Morang | DoverDC |  | DoverDC (Dover1 SM2 Pty Ltd) | VIC | South Morang, Melbourne | 165 Williamsons Road, South Morang VIC 3752 | -37.647 | 145.087 | Planning | Hyperscale | 2026 |  | 0 | 200 | 8.7 |  | Undisclosed | Adjacent to South Morang Terminal Station and substation; application filed Aug 2026 with Victorian Department of Transport and Planning |  |  | A 200MW, three-storey second DoverDC facility proposed on 8.7ha next to the South Morang Terminal Station, filed August 2026 amid Whittlesea Council calls for greater oversight. | DoverDC在South Morang终端站旁8.7公顷土地上提出的第二座设施，200 MW、三层，2026年8月递交申请，Whittlesea Council呼吁加强监管。 | https://www.datacenterdynamics.com/en/news/application-filed-for-200mw-data-center-in-melbourne-australia/ ¦ https://w.media/whittlesea-seeks-greater-oversight-as-dover-plans-200mw-victorian-facility/ | 2026-09-15 | IT load
equinix-me4 | Equinix ME4 Derrimut | Equinix | equinix | Equinix | VIC | Derrimut, Melbourne | 2 Davis Court, Derrimut VIC 3026 | -37.793 | 144.766 | Operational | Colocation | 2018 | 2019 |  |  |  |  | Enterprise, government, cloud | Former Metronode facility acquired 2018; expansion phases in Melbourne's west | air | Uptime Tier III (Metronode heritage), ISO 27001, PCI DSS | Equinix's largest Melbourne IBX, the former Metronode Derrimut facility, providing carrier-neutral colocation in the western hyperscale corridor. | Equinix在墨尔本最大的IBX，原为Metronode的Derrimut设施，在西部超大规模走廊提供运营商中立托管服务。 | https://www.equinix.com/data-centers/asia-pacific-colocation/australia-colocation/melbourne-data-centers/me4 ¦ https://baxtel.com/data-center/equinix-me4 | 2026-09-15 | IT load
goodman-truganina | Goodman Truganina Data Centre Campus | Goodman Group | goodman | Goodman Group | VIC | Truganina, Melbourne | 433 Mount Atkinson Road, Truganina VIC 3029 | -37.777 | 144.713 | Planning | Hyperscale | 2026 |  | 0 |  |  |  | Undisclosed hyperscaler | Three two-storey data centre buildings; plans lodged July 2026 on land acquired from ESR; capacity not disclosed |  |  | Goodman's first Melbourne data centre campus, a three-building proposal at Mount Atkinson Road in the established Truganina hyperscale corridor lodged in July 2026. | Goodman在墨尔本的首个数据中心园区，位于Truganina成熟超大规模走廊的Mount Atkinson Road，规划三栋楼，2026年7月递交申请，容量未披露。 | https://w.media/victorias-data-centre-pipeline-grows-with-four-new-melbourne-proposals/ ¦ https://certifiedstrategic.com/insights/melbourne-data-centre-pipeline-four-new-campuses | 2026-09-15 | IT load
microsoft-tullamarine | Microsoft Garden Drive Tullamarine (MEL07) | Microsoft | microsoft | Microsoft | VIC | Tullamarine, Melbourne | 70-90 Garden Drive, Tullamarine VIC 3043 | -37.706 | 144.859 | Under Construction | Hyperscale campus (self-build) | 2023 | [5 empty] | Microsoft Azure | Self-build Azure facility near Melbourne Airport; part of Microsoft's A$5bn Australian data centre programme |  |  | Microsoft's self-built Azure facility at Garden Drive, Tullamarine, one of several Melbourne sites under its A$5bn Australian cloud and AI infrastructure investment. | 微软在Tullamarine Garden Drive自建的Azure设施，目前在建，是其50亿澳元澳洲云与AI基础设施投资中的墨尔本站点之一。 | https://local.microsoft.com/blog/garden-drive-datacentre-construction-overview/ ¦ https://www.datacentermap.com/australia/melbourne/ | 2026-09-15 | IT load
microsoft-truganina | Microsoft Woods Road Truganina | Microsoft | microsoft | Microsoft | VIC | Truganina, Melbourne | 281 Woods Road, Truganina VIC 3029 | -37.799 | 144.728 | Operational | Hyperscale campus (self-build) | 2022 | 2025 |  |  |  |  | Microsoft Azure | On-site substation via AusNet; construction Dec 2022 to mid-2025 (Kapitol Group / BESIX Watpac) |  |  | Microsoft's self-built Azure data centre on Woods Road, Truganina, constructed 2022-2025 with an on-site AusNet substation, part of the Australia Southeast region expansion. | 微软在Truganina Woods Road自建的Azure数据中心，2022–2025年建设，配套AusNet场内变电站，属Australia Southeast区域扩容的一部分。 | https://local.microsoft.com/blog/woods-road-datacentre-construction-overview/ ¦ https://www.datacentermap.com/australia/melbourne/microsoft-woods-road/ | 2026-09-15 | IT load
microsoft-yarraville | Microsoft Yarraville Campus (MEL04 / MEL05 Cawley Road) | Microsoft | microsoft | Microsoft | VIC | Yarraville, Melbourne | 20-28 Cawley Road, Yarraville VIC 3013 | -37.82 | 144.87 | Under Construction | Hyperscale campus (self-build) | 2022 |  |  |  | 13 | 150 | Microsoft Azure | 13ha site bought for A$90m (2021); MEL04 first building (A$150m) approved, MEL05 to follow; part of Microsoft's A$5bn Australian investment |  |  | Microsoft's self-built inner-west Melbourne cloud campus on a 13ha former industrial site in Yarraville, with the first A$150m building (MEL04) approved and a second (MEL05) planned. | 微软在墨尔本内西区Yarraville 13公顷原工业用地上自建的云园区，首栋楼MEL04（投资1.5亿澳元）已获批，MEL05随后跟进。 | https://www.datacenterdynamics.com/en/news/microsoft-planning-data-centers-in-melbourne-australia/ ¦ https://local.microsoft.com/blog/cawley-road-datacentre-construction-overview/ ¦ https://www.theurbandeveloper.com/articles/microsoft-lodges-plans-yarraville-data-centre | 2026-09-15 | IT load
nextdc-ge1 | NEXTDC GE1 Geelong | NEXTDC | nextdc | NEXTDC | VIC | Corio, Geelong | Corio, Geelong VIC 3214 | -38.09 | 144.37 | Under Construction | Edge | 2024 |  | 0 | 4.4 |  |  | Regional enterprise, government | Regional edge site; 4.4MW design | air | Target Uptime Tier III | NEXTDC's 4.4MW regional edge data centre in Geelong, the first purpose-built colocation facility for the Geelong/Surf Coast region. | NEXTDC在Geelong Corio在建的4.4 MW区域边缘数据中心，是Geelong/Surf Coast地区首座专建托管设施。 | https://www.datacenterdynamics.com/en/news/nextdc-breaks-ground-on-44mw-edge-data-center-in-geelong-australia/ ¦ https://www.nextdc.com/data-centres | 2026-09-15 | IT load
nextdc-m1 | NEXTDC M1 Port Melbourne | NEXTDC | nextdc | NEXTDC | VIC | Port Melbourne, Melbourne | 826 Lorimer Street, Port Melbourne VIC 3207 | -37.827 | 144.9105 | Operational | Colocation | 2011 | 2012 | 16 | 16 |  |  | Enterprise, government, cloud on-ramps (AWS, Azure, Google) | Dual utility feeds; NEXTDC 100% renewable electricity via certificates | air | Uptime Tier III Design & Constructed Facility, ISO 27001, PCI DSS, SOC 2 | NEXTDC's original Melbourne colocation facility in the Fishermans Bend precinct, a 16MW carrier-dense interconnection hub for enterprise and cloud on-ramps. | NEXTDC在墨尔本的首座托管设施，位于Fishermans Bend片区，2012年投运，IT负载16 MW，运营商密集，是企业和云接入的互联枢纽。 | https://www.nextdc.com/data-centres ¦ https://www.datacentermap.com/australia/melbourne/ | 2026-09-15 | IT load
nextdc-m2 | NEXTDC M2 Tullamarine | NEXTDC | nextdc | NEXTDC | VIC | Tullamarine, Melbourne | 75 Sharps Road, Tullamarine VIC 3043 | -37.711 | 144.87 | Operational | Colocation | 2016 | 2017 |  | 120 |  |  | Hyperscale cloud, enterprise, government | Dedicated on-site zone substation; 120MW+ IT design capacity after multiple upsizings | hybrid | Uptime Tier IV Certified Constructed Facility, Tier IV Gold Operational Sustainability, ISO 27001, PCI DSS | NEXTDC's Tier IV flagship near Melbourne Airport, upsized from 25MW to a 120MW+ design and serving hyperscale cloud availability zones alongside enterprise colocation. | NEXTDC在墨尔本机场附近的Tier IV旗舰，设计容量由最初25 MW多次上调至120 MW以上，同时承载超大规模云可用区和企业托管业务。 | https://www.nextdc.com/data-centres/melbourne-data-centres/m2-melbourne ¦ https://renewmap.com.au/resources/projects/vic/datacentre/ | 2026-09-15 | IT load
nextdc-m3 | NEXTDC M3 West Footscray | NEXTDC | nextdc | NEXTDC | VIC | West Footscray, Melbourne | 25 Indwe Street, West Footscray VIC 3012 | -37.7965 | 144.862 | Operational | Colocation | 2020 | 2023 |  | 225 |  |  | Hyperscale cloud, AI, enterprise | Staged build-out; ~133MW of additional capacity under construction in 2026 against forward-contracted demand | liquid-ready | Uptime Tier IV Design (target Constructed), ISO 27001, PCI DSS | NEXTDC's largest Melbourne asset, a 225MW-design hyperscale-grade colocation campus in West Footscray that opened in 2023 and is still being built out in stages against contracted demand. | NEXTDC在墨尔本最大的资产，位于West Footscray，设计容量225 MW，2023年开业，目前按已签约需求分期建设。 | https://www.nextdc.com/data-centres/melbourne-data-centres/m3-melbourne ¦ https://itkservices3.com/background/data_centres_australia_top10_construction | 2026-09-15 | IT load
nextdc-m4 | NEXTDC M4 Port Melbourne | NEXTDC | nextdc | NEXTDC | VIC | Port Melbourne (Fishermans Bend), Melbourne | 127 Todd Road, Port Melbourne VIC 3207 | -37.8305 | 144.913 | Approved | Colocation | 2024 |  | 0 | 150 | 2.64 |  | Hyperscale cloud, enterprise, government (target) | 150MW IT design on a 26,400 sqm Fishermans Bend site; power allocation being secured VIC ministerial permit PA2504019 (127 Todd Road, Port Melbourne) approved 16 Jan 2026 under the Development Facilitation Program. | liquid-ready | Target Uptime Tier IV, NVIDIA-certified AI Factory design | Planned 150MW inner-city AI-ready facility at Fishermans Bend, adjacent to M1, designed to Tier IV standards for hyperscale and regulated workloads. | NEXTDC规划中的150 MW市区AI就绪设施，位于Fishermans Bend、紧邻M1，按Tier IV设计，面向超大规模云和受监管工作负载；供电容量分配正在落实。 | https://www.nextdc.com/data-centres/melbourne-data-centres/m4-melbourne ¦ https://www.datacentermap.com/australia/melbourne/ | 2026-10-07 | IT load
stack-mel01 | STACK MEL01 Truganina | STACK Infrastructure | stack-infrastructure | Blue Owl Capital (IPI Partners) / STACK Infrastructure | VIC | Truganina, Melbourne | 399 Palmers Road, Truganina VIC 3029 | -37.808 | 144.737 | Operational | Hyperscale | 2022 | 2023 | 72 | 180 | 3.6 |  | Undisclosed hyperscaler | MEL01A and MEL01B (36MW each) complete; MEL01C and MEL01D (54MW each) under construction; A$1.3bn green financing (Jul 2025) | hybrid |  | STACK's debut Australian campus in Truganina: four buildings totalling 180MW, with 72MW (MEL01A/B) live and MEL01C/D under construction funded by a A$1.3bn green loan. | STACK在澳洲的首个园区，位于Truganina，四栋楼合计180 MW，其中MEL01A/B共72 MW已投运，MEL01C/D在建，由13亿澳元绿色贷款支持。 | https://www.datacenterdynamics.com/en/news/stack-tops-out-swiss-data-center-completes-construction-in-melbourne/ ¦ https://www.datacenterdynamics.com/en/news/stack-secures-au13bn-green-financing-in-australia-to-fund-melbourne-campus/ ¦ https://www.stackinfra.com/locations/asia-pacific/melbourne/mel01/ | 2026-09-15 | IT load
stack-mel02 | STACK MEL02 Truganina | STACK Infrastructure | stack-infrastructure | Blue Owl Capital (IPI Partners) / STACK Infrastructure | VIC | Truganina, Melbourne | Wyndham Industrial Estate, Truganina VIC 3029 | -37.823 | 144.733 | Under Construction | Hyperscale | 2023 |  |  | 252 | 5.7 |  | Undisclosed hyperscaler | Single 21,000 sqm building on 14-acre site; construction completion targeted late 2025 with in-service 2026 | liquid-ready |  | STACK's second Melbourne campus, a single-building 252MW hyperscale facility in Truganina near MEL01, scheduled to enter service during 2026. | STACK的第二座墨尔本园区，位于Truganina、临近MEL01，为单体252 MW超大规模设施，计划2026年投入运营。 | https://www.stackinfra.com/locations/asia-pacific/melbourne/mel02/ ¦ https://www.datacentermap.com/australia/melbourne/stack-infrastructure-mel02/ ¦ https://itkservices3.com/background/data_centres_australia_top10_construction | 2026-09-15 | IT load
stockland-brooklyn | Stockland Brooklyn Distribution Centre Data Centre | Stockland / EdgeConneX | stockland | Stockland | VIC | Brooklyn, Melbourne | Brooklyn Distribution Centre, Millers Road, Brooklyn VIC 3012 | -37.819 | 144.843 | Planning | Hyperscale | 2026 |  | 0 | 100 |  |  | Undisclosed hyperscaler | Second of two Melbourne sites with ~350MW total secured power (Feb 2026); ~100MW implied after the 250MW Cherry Lane allocation (derived, not officially stated) |  |  | Stockland's second Melbourne data centre conversion site at its Brooklyn logistics estate, with roughly 100MW implied from the ~350MW of grid power secured across both Melbourne sites. | Stockland在Brooklyn物流园的第二个墨尔本数据中心改造用地；按其在两个墨尔本站点合计锁定约350 MW电力推算，该站点约100 MW（推算值，未经官方公布）。 | https://www.datacenterdynamics.com/en/news/stockland-files-to-develop-250mw-data-center-campus-in-melbourne-australia/ ¦ https://w.media/stockland-finalises-edgeconnex-data-centre-jv-as-ceo-plots-more-investment/ | 2026-09-15 | IT load
stockland-laverton-cherry-lane | Stockland Laverton Data Centre Campus (Cherry Lane) | Stockland / EdgeConneX | stockland | Stockland | VIC | Laverton North, Melbourne | 72-76 Cherry Lane, Laverton North VIC 3026 | -37.833 | 144.783 | Planning | Hyperscale | 2026 |  | 0 | 250 |  | 2000 | Undisclosed hyperscaler | Part of ~350MW of grid power Stockland secured across two Melbourne sites (Cherry Lane and Brooklyn Distribution Centre) announced Feb 2026; planning permit filed May 2026 | liquid-ready |  | Stockland's 250MW, two-building hyperscale campus proposed on a former Toll Transport site in Laverton North, its first Melbourne data centre development under the EdgeConneX partnership. | Stockland在Laverton North原Toll Transport用地上提出的250 MW双楼超大规模园区，是其与EdgeConneX合作后在墨尔本的首个数据中心项目，规划许可2026年5月递交。 | https://www.datacenterdynamics.com/en/news/stockland-files-to-develop-250mw-data-center-campus-in-melbourne-australia/ ¦ https://www.realestatesource.com.au/stockland-proposes-major-melbourne-data-centre/ | 2026-09-15 | IT load
vantage-mel1 | Vantage MEL1 Tullamarine | Vantage Data Centers |  | Vantage Data Centers (DigitalBridge / Silver Lake) | VIC | Tullamarine, Melbourne | 45 Tullamarine Park Road, Tullamarine VIC 3043 | -37.703 | 144.852 | Under Construction | Hyperscale | 2024 |  | 0 | 64 | 3 |  | Undisclosed hyperscaler | On-campus 66kV substation; N+1; hybrid chilled water with economiser; 2026 commissioning targeted | hybrid |  | Vantage's first Australian facility, a 64MW single-building hyperscale data centre 6km from Melbourne Airport, targeting 2026 commissioning; a second Melbourne site (MEL2) has been flagged. | Vantage在澳洲的首个设施，位于Tullamarine、距墨尔本机场6 km，单体64 MW，目标2026年投运；公司已预告将在墨尔本开发第二个站点MEL2。 | https://vantage-dc.com/data-center-locations/apac/melbourne-australia/ ¦ https://www.datacentermap.com/australia/melbourne/vantage-mel1-melbourne/ | 2026-09-15 | IT load
victorian-ai-hub-plumpton | Victorian AI Hub (Plumpton) | Undisclosed |  | Undisclosed (assembled landholding) | VIC | Plumpton, Melbourne (west) | Plumpton VIC 3335 (green wedge, west of Caroline Springs) | -37.715 | 144.69 | Planning | Hyperscale | 2026 |  | 0 | 2400 | 350 |  | Undisclosed | Reported ~2,400MW gigawatt-scale AI campus on ~350ha of assembled green-wedge land; subject to parliamentary petition seeking full assessment (closes Nov 2026) |  |  | A reported gigawatt-scale (~2.4GW) AI data centre hub proposed on ~350ha of green-wedge land at Plumpton in Melbourne's west, currently the largest single item in Victoria's pipeline and the subject of a Victorian Parliament petition. | 据报道拟在墨尔本西部Plumpton约350公顷绿楔用地上开发的吉瓦级（约2.4 GW）AI数据中心枢纽，是维州管线中规模最大的单一项目，目前有维州议会请愿要求进行全面评估。 | https://www.parliament.vic.gov.au/get-involved/petitions/fully-assess-planning-decision-for-a-proposed-victorian-ai-hub/ ¦ https://renewmap.com.au/resources/projects/vic/datacentre/ | 2026-09-15 | Site/grid power
zerra-campbellfield | Zerra DC Melbourne Campus (former Ford Broadmeadows plant) | Zerra DC |  | Zerra DC (AGP) | VIC | Campbellfield, Melbourne | 300-340 Barry Road, Campbellfield VIC 3061 | -37.676 | 144.952 | Planning | Hyperscale | 2026 |  | 0 |  | 18.2 |  | AI / cloud (target) | Six-building AI and cloud campus; planning permit filed April 2026; EPA has raised objections; strong local opposition |  |  | Singapore-based Zerra DC's first Australian project: a six-building AI and cloud campus on the 45-acre former Ford Falcon assembly plant in Campbellfield, filed April 2026 and facing EPA and community objections. | 新加坡Zerra DC在澳洲的首个项目：在Campbellfield约45英亩原Ford Falcon装配厂用地上建设六栋楼的AI与云园区，2026年4月递交规划申请，面临EPA和社区反对。 | https://www.datacenterdynamics.com/en/news/zerra-dc-files-to-build-six-building-data-center-campus-in-melbourne-australia/ ¦ https://www.abc.net.au/news/2026-08-26/proposal-to-turn-former-ford-factory-into-giant-data-centre/107075906 | 2026-09-15 | IT load
cdc-maddington | CDC Maddington Campus | CDC Data Centres | cdc | Infratil / Future Fund / CSC (CDC Data Centres) | WA | Maddington, Perth | 307 Kenwick Road, Maddington WA 6109 | -32.028 | 115.987 | Under Construction | Hyperscale | 2024 |  | 0 | 200 |  | 415 | Australian Government / Defence (AUKUS-aligned), undisclosed hyperscaler | Four-building campus (DC1-DC4) to 200MW; stage one A$415m targeted operational 2026; closed-loop zero-water primary cooling; liquid-cooling ready | liquid-ready | Target Hosting Certification Framework Certified Strategic, DISP | CDC's first Western Australian campus, a 200MW four-building AI and sovereign-cloud precinct in Maddington 20km south-east of Perth, with the A$415m first stage due to open in 2026 and positioned for AUKUS-related demand. | CDC在西澳的首个园区，位于珀斯东南20 km的Maddington，四栋楼合计200 MW，面向AI和主权云；首期投资4.15亿澳元，计划2026年投运，并瞄准AUKUS相关需求。 | https://www.datacenterdynamics.com/en/news/australias-cdc-plans-200mw-data-center-campus-outside-perth/ ¦ https://w.media/cdc-data-centres-plans-was-largest-ai-and-advanced-technology-campus/ ¦ https://www.datacentermap.com/australia/perth/cdc-maddington-campus/ | 2026-09-15 | IT load
dca-pier-canning-vale | DC Alliance PIER Canning Vale | DC Alliance |  | DC Alliance | WA | Canning Vale, Perth | 1 Martin Place, Canning Vale WA 6155 | -32.063 | 115.908 | Operational | Colocation |  |  | 6 | 8 |  |  | Enterprise, resources, government | Independent Perth colocation facility; ~6-8MW | air | Uptime Tier III (design) | DC Alliance's PIER facility in Canning Vale, one of the larger independent colocation sites in southern Perth at around 6-8MW. | DC Alliance在珀斯南部Canning Vale的PIER设施，约6–8 MW，是当地规模较大的独立托管站点之一。 | https://www.datacentermap.com/australia/perth/ ¦ https://renewmap.com.au/resources/projects/wa/datacentre/ | 2026-09-15 | IT load
equinix-pe2-pe3 | Equinix PE2/PE3 Shenton Park | Equinix | equinix | Equinix | WA | Shenton Park, Perth | 37 Lemnos Street, Shenton Park WA 6008 | -31.956 | 115.799 | Operational | Colocation | 2019 | 2021 |  |  |  | 76 | Carriers, cloud, enterprise, subsea cable operators (INDIGO West landing) | PE3 (A$76m, opened Dec 2021) adjoins PE2; key interconnection point for INDIGO and other Perth subsea systems | air | ISO 27001, PCI DSS, SOC | Equinix's Shenton Park campus (PE2 and the A$76m PE3 opened in 2021), Perth's densest interconnection hub and the landing point ecosystem for Indian Ocean subsea cables. | Equinix在Shenton Park的园区（PE2及2021年开业、投资7,600万澳元的PE3），是珀斯互联密度最高的枢纽，也是印度洋海缆登陆的核心生态节点。 | https://www.equinix.com/data-centers/asia-pacific-colocation/australia-colocation/perth-data-centers/pe3 ¦ https://www.businessnews.com.au/article/Equinix-plans-76m-Perth-expansion | 2026-09-15 | IT load
nextdc-p1 | NEXTDC P1 Malaga | NEXTDC | nextdc | NEXTDC | WA | Malaga, Perth | 4 Millrose Drive, Malaga WA 6090 | -31.856 | 115.899 | Operational | Colocation | 2012 | 2014 | 10 | 10 |  |  | Resources sector, enterprise, government | Dual Western Power feeds; 10MW+ IT design | air | Uptime Tier III Certified, ISO 27001, PCI DSS | NEXTDC's first Perth facility in the Malaga industrial area, a 10MW+ Tier III colocation site serving the resources sector and enterprise. | NEXTDC在珀斯的首座设施，位于Malaga工业区，2014年投运，10 MW以上、Tier III，服务资源行业和企业客户。 | https://www.nextdc.com/data-centres ¦ https://www.datacentermap.com/australia/perth/ | 2026-09-15 | IT load
nextdc-p2 | NEXTDC P2 Perth CBD | NEXTDC | nextdc | NEXTDC | WA | Perth CBD | 11 Newcastle Street, Perth WA 6000 | -31.947 | 115.856 | Operational | Colocation | 2018 | 2020 |  | 20 |  |  | Cloud on-ramps, government, enterprise | 20MW+ IT design; Tier IV | air | Uptime Tier IV Certified Constructed Facility, ISO 27001 | NEXTDC's Tier IV Perth CBD facility with 20MW+ design capacity, the city's main cloud on-ramp and interconnection hub. | NEXTDC在珀斯CBD的Tier IV设施，2020年投运，设计容量20 MW以上，是珀斯主要的云接入和互联枢纽。 | https://www.nextdc.com/data-centres ¦ https://renewmap.com.au/resources/projects/wa/datacentre/ | 2026-09-15 | IT load
gingerah-project-meridien | Project Meridien (Gingerah Energy Hub AI Data Centre) | Gingerah Energy |  | Gingerah Energy (Karajarri Traditional Lands Association / Fugro / Longreach Capital JV) | WA | Gingerah, Kimberley (south of Broome) | Karajarri country, south of Broome, Kimberley WA | -18.9 | 121.9 | Planning | Hyperscale | 2026 |  | 0 | 1000 | 27500 |  | AI hyperscalers (target) | Off-grid: on-site wind, solar, batteries and gas; initial ~240MW IT phase then up to 1GW; closed-loop cooling; EPA referral pending; construction from late 2029, opening ~2032 | liquid-ready |  | A gigawatt-scale renewable-powered AI factory proposed on Karajarri country south of Broome by Gingerah Energy (Traditional Owners, Fugro and Longreach), with a ~240MW first phase targeted for 2032. | Gingerah Energy（Karajarri传统土地所有者、Fugro与Longreach合资）拟在Broome以南Karajarri土地上建设的吉瓦级可再生能源AI工厂，首期约240 MW，目标2032年投运。 | https://www.abc.net.au/news/2026-04-20/plans-emerge-gigawatt-scale-ai-data-centre-kimberley/106567332 ¦ https://wainvestments.com.au/projects/gingerah-energy-hub/ | 2026-09-15 | Site generation
stack-perth | STACK Perth Campus (PER01/PER02) Wangara | STACK Infrastructure | stack-infrastructure | Blue Owl Capital (IPI Partners) / STACK Infrastructure | WA | Wangara, Perth | 92 Windsor Road, Wangara WA 6065 | -31.79 | 115.836 | Operational | Colocation | 2022 | 2015 | 8 | 24 |  |  | Enterprise, resources, cloud | PER01 (8MW, ex-DC Two/Hyperscale) operating; PER02 (16MW) expansion; 24MW campus total | air | Uptime Tier III | STACK's Perth campus in Wangara, built around the former DC Two facility, with 8MW live (PER01) and a 16MW PER02 expansion for a 24MW total. | STACK在珀斯北部Wangara的园区，以原DC Two设施为基础，PER01已运营8 MW，PER02扩建16 MW，园区合计24 MW。 | https://baxtel.com/data-center/stack-perth-per01 ¦ https://www.datacentermap.com/australia/perth/ | 2026-09-15 | IT load
cdc-gregadoo-wagga | CDC Ashfords Road Campus, Gregadoo (Wagga Wagga) | CDC Data Centres | cdc | CDC Data Centres (Infratil / Commonwealth Superannuation Corp backed) | NSW | Gregadoo (Wagga Wagga) | 216 Ashfords Road, Gregadoo NSW 2650 | -35.217 | 147.366 | Planning | Hyperscale campus (self-build) | 2026 |  | 0 | 1400 | 103.4 | 15000 |  | Two on-site substations proposed; site is 1.3km from Transgrid's new Wagga Wagga Terminal Station. 384 standby diesel generators and 13MW of rooftop solar proposed. Grid capacity still to be established; land requires rezoning from rural. | Closed-loop mechanical cooling |  | CDC Data Centres lodged a SEARs application (SSD-144289240) on 21 September 2026 for a campus of up to 1.4GW on 103.4 hectares at 216 Ashfords Road, Gregadoo, about 11km south of Wagga Wagga, with capex of up to A$15 billion. Four single-storey buildings totalling 189,325sqm would be delivered at roughly 240MW each, with the pipeline running to 2034. | CDC Data Centres 于 2026 年 9 月 21 日就 216 Ashfords Road, Gregadoo 递交 SEARs 申请（SSD-144289240），用地 103.4 公顷，位于 Wagga Wagga 以南约 11 km，满建容量 1.4 GW，资本开支最高 150亿澳元。四栋单层厂房合计 189,325 ㎡，单栋约 240 MW，分期落地至 2034 年。场地距 Transgrid 新建的 Wagga Wagga Terminal Station 仅 1.3 km，自建两座变电站，配 384 台柴发与 13 MW 屋顶光伏；用地目前仍为 rural 分区，需先行调整规划，电网容量亦待落实。 | https://www.datacenterdynamics.com/en/news/australias-cdc-plans-gigawatt-scale-data-center-campus-in-wagga-wagga/ ¦ https://www.abc.net.au/news/2026-09-30/15-billion-dollar-data-centre-proposed-for-wagga-wagga/107191146 ¦ https://www.mingtiandi.com/real-estate/data-centres/cdc-proposes-10-5b-new-south-wales-data-centre/ ¦ https://urbandigest.com.au/urban-digest-weekly-57-nsw-ssd-updates-21-september-2026/ ¦ https://haveyoursay.wagga.nsw.gov.au/ashford-road-gregadoo-data-centre-proposal | 2026-10-07 | IT load
hyperdc-moorabool | HyperDC Moorabool Campus (715 Ballan Road) | HyperDC Pty Ltd | hyperdc | HyperDC Pty Ltd | VIC | Moorabool (Geelong) | 715 Ballan Road, Moorabool VIC 3213 | -38.017 | 144.25 | Planning | Hyperscale | 2026 |  | 0 | 400 | 39 |  |  | Site adjoins AusNet's Moorabool Terminal Station and sits beside the 300MW Victorian Big Battery; grid connection is the stated rationale for the location. No PPA or connection agreement disclosed. |  |  | HyperDC filed a planning permit application with the Victorian government on 29 September 2026 for a 400MW IT load campus on 39 hectares at 715 Ballan Road, Moorabool, about 75km west of Melbourne. Little is publicly known about the proponent; the site's appeal is its position next to AusNet's Moorabool Terminal Station and the Victorian Big Battery. | HyperDC 于 2026 年 9 月 29 日向维州递交规划许可申请，拟在墨尔本以西约 75 km 的 715 Ballan Road, Moorabool 开发 39 公顷园区，IT负载 400 MW。场地紧邻 AusNet 的 Moorabool Terminal Station 与 300 MW 的 Victorian Big Battery，并网条件是选址的核心理由。开发商背景公开信息有限，资本开支、冷却方案与租户均未披露；申请递交时点正值维州 Sustainable Data Centre Action Plan 收紧新规，审批路径存在不确定性。 | https://www.datacenterdynamics.com/en/news/plans-filed-for-400mw-data-center-campus-outside-melbourne-australia/ ¦ https://baxtel.com/news/hyperdc-files-plans-for-400mw-data-center-campus-west-of-melbourne | 2026-10-07 | IT load
cdc-beard-two | CDC Beard 2 (BE2) | CDC Data Centres | cdc | CDC Data Centres (Infratil / Commonwealth Superannuation Corp backed) | ACT | Beard | 23 Tantalum Street, Beard ACT 2620 (Block 25 Section 11) | -35.337 | 149.224 | Approved | Hyperscale | 2026 |  | 0 | 84 |  | 203.5 |  | Up to 20MW of emergency on-site generation; a future 3,830sqm substation is included in the approved scheme. Conditions cover water use and energy monitoring. |  |  | The ACT Territory Planning Authority granted conditional development approval on 30 September 2026 for CDC's Beard 2, an 84MW three-storey facility with 12 data halls and 29,924sqm GFA at 23 Tantalum Street, Beard, costing A$203.5 million. It is the second stage of the Beard campus alongside the 39MW Beard 1; a construction start has not been confirmed. | ACT Territory Planning Authority 于 2026 年 9 月 30 日对 CDC 的 Beard 2 发出附条件批复：三层建筑、12 个机房、建筑面积 29,924 ㎡、占地面积 10,357 ㎡，IT负载 84 MW，造价 2.035亿澳元，地址 23 Tantalum Street, Beard（Block 25 Section 11）。该栋为 Beard 园区二期，与 10 个机房、15,348 ㎡ 的 Beard 1 同场，建成后园区建筑面积约 45,272 ㎡。方案含最高 20 MW 应急发电及后续 3,830 ㎡ 变电站，批复条件涵盖污染治理、噪声控制与用水监测；开工时间尚未确认。 | https://w.media/cdc-wins-approval-for-au203-5m-beard-2-data-centre-in-canberra/ ¦ https://www.cmtedd.act.gov.au/open_government/inform/act_government_media_releases/barr/2026/providing-a-clear-framework-for-data-centres-in-the-act | 2026-10-07 | IT load
stockland-khartoum-road-1 | Stockland Road 1 Data Centre, Macquarie Park (1-5 Khartoum Road) | Stockland | stockland | Stockland Development Pty Ltd | NSW | Macquarie Park | 1-5 Khartoum Road, Macquarie Park NSW 2113 | -33.778 | 151.124 | Approved | Colocation | 2026 |  | 0 | 34.3 |  | 630.4 |  | 49MW maximum electrical demand against 34.3MW IT load. Consent caps standby generator operation at 55.4 hours a year excluding emergencies, and requires renewable offsets for operational emissions. |  | Design targets: PUE 1.35, five-star NABERS | NSW DPHI determined SSD-80814238 on 1 October 2026, approving Stockland's 10-storey (72.8m) 'Road 1' data centre at 1-5 Khartoum Road, Macquarie Park: 34.3MW IT load across eight data halls, 49MW maximum demand and A$630.4 million capex. It is a separate building from the 76.4MW Stockland data centre approved immediately to the north-west in March 2026. | NSW DPHI 于 2026 年 10 月 1 日核准 SSD-80814238：Stockland 可在 1-5 Khartoum Road, Macquarie Park 建设十层、最高 72.8 m 的 Road 1 数据中心，8 个机房、IT负载 34.3 MW，最大需量 49 MW，造价 6.304亿澳元。批复设定 PUE 1.35 与 NABERS 五星目标，限定柴发年运行 55.4 小时（应急除外），并要求以可再生电力抵消运营排放。该栋与 Stockland 于 2026 年 3 月在同一地块西北侧获批的 76.4 MW 项目（SSD-63235720）为两宗独立开发。 | https://urbandigest.com.au/ssd-80814238-630m-macquarie-park-data-centre-approved/ ¦ https://w.media/stockland-wins-approval-for-49mw-10-storey-macquarie-park-data-centre/ ¦ https://urbandigest.com.au/ssd-63235720-1-5-khartoum-road-data-centre/ | 2026-10-07 | IT load
sharonai-ettamogah-albury | SharonAI Ettamogah Site (former Visy paper mill) | SharonAI |  | SharonAI (Nasdaq-listed) | NSW | Ettamogah (Albury) | R W Henry Drive, Ettamogah NSW 2640 | -36.005 | 146.943 | Planning | Hyperscale | 2026 |  | 0 |  |  | 50 |  | Not disclosed. Brownfield industrial site (former Australian Newsprint Mills / Norske Skog / Visy paper mill, closed late 2019) with legacy heavy-industrial supply. |  |  | SharonAI acquired the former Visy paper mill on R W Henry Drive at Ettamogah, north of Albury, for about A$50 million in September 2026, saying it would return the brownfield site to a running operation. No capacity, power arrangement or timeline has been disclosed, and Visy remains as a warehouse and logistics tenant. | SharonAI 于 2026 年 9 月以约 5,000万澳元买下 Albury 以北 Ettamogah 的 R W Henry Drive 旧 Visy 纸厂（前身为 Australian Newsprint Mills、Norske Skog，2019 年底停产），表示将把这块棕地重新投入运营。容量、供电方案与时间表均未披露，Visy 保留仓储物流租约。SharonAI 目前在 Equinix 悉尼与 NEXTDC 墨尔本承租算力，并于 2026 年 9 月与 GreenSquareDC 的 SYD1 签订长期合同，全球在运及在建规模 212 MW，计划到 2027 年中部署约 64,000 颗 Nvidia GPU。 | https://www.datacenterdynamics.com/en/news/sharonai-buys-former-printing-press-outside-albury-australia/ | 2026-10-07 | IT load
keppel-morwell-latrobe | Keppel Morwell AI Data Centre Campus (Latrobe Valley) | Keppel Data Centres |  | Keppel Ltd (site held under agreement for lease from Lightwood Group) | VIC | Morwell (Latrobe Valley) | Former Hazelwood power station precinct, Brodribb Road area, Morwell VIC 3840 (exact parcel not disclosed) | -38.2767 | 146.3889 | Planning | Hyperscale AI campus (wholesale / build-to-suit) | 2026 |  | 0 | 720 | 123 | 10000 |  | 720MW is gross site power capacity, not IT load; IT load has not been disclosed. Keppel proposes a dedicated transmission connection to nearby terminal stations, which would let future phases bypass the local distribution network. The site sits inside the proposed Gippsland Renewable Energy Zone at one of Victoria's largest electricity nodes, next to the retired Hazelwood and operating Loy Yang generation. Land is taken progressively under an annual access fee, converting to long-term leases once customer demand is secured. | Non-potable water cooling proposed using existing Latrobe Valley water infrastructure; design not disclosed |  | Keppel secured site control on 16 January 2026 over a 123-hectare contiguous holding near Morwell, about 152km east of Melbourne, for a 720MW gross 'powerbank' AI campus costed in press reports at around A$10 billion. The land is held from Lightwood Group on an annual access fee with long-term leases to follow as customers are signed. Keppel cites proximity to intercity dark fibre between Melbourne, Sydney and Canberra, non-potable water for cooling, and competitively priced green power. No planning application has been lodged with Latrobe City Council; discussions with hyperscale and neocloud operators are described as pre-development. | Keppel 于 2026 年 1 月 16 日取得 Morwell 附近 123 公顷整块用地的控制权，场地位于墨尔本以东约 152 km，规划为 720 MW 毛容量的 AI 园区，媒体口径资本开支约 100亿澳元。土地由 Lightwood Group 持有，目前按年支付进场费，锁定租户后转为长租。Keppel 看重三点：紧邻 Melbourne-Sydney-Canberra 城际暗光纤、可取用非饮用水做冷却、以及 Gippsland Renewable Energy Zone 内相对低价的绿电。场地紧靠已退役的 Hazelwood 与在运的 Loy Yang 机组，计划自建专用输电接入直连邻近 terminal station，后续分期可绕开本地配电网。720 MW 为场地毛供电能力，IT负载未披露。尚未向 Latrobe City Council 递交规划许可申请，与超大规模及 neocloud 客户仍处前期洽谈。 | https://www.abc.net.au/news/2026-01-22/keppel-data-centre-latrobe-valley/106123748 ¦ https://w.media/keppel-secures-720mw-powerbank-site-near-melbourne-for-ai-dc-campus/ ¦ https://www.datacenterdynamics.com/en/news/keppel-secures-rights-to-720mw-data-center-campus-outside-melbourne-australia/ ¦ https://www.energymagazine.com.au/keppel-to-build-720mw-data-centre-near-victorian-coal-plants/ ¦ https://www.datacentermap.com/australia/morwell/keppel-dc-morwell/ | 2026-10-07 | Site/grid power
pgim-truganina-oroya | PGIM Truganina Data Centre Campus (1 Oroya Drive) | Not appointed (PGIM Real Estate as developer) |  | PGIM Real Estate Global Data Centre Fund | VIC | Truganina | 1 Oroya Drive, Truganina VIC 3029 | -37.8213 | 144.7389 | Planning | Wholesale / hyperscale campus (three phases) | 2026 |  | 0 | 80 | 20.7 | 1200 |  | 80MW is the first-phase figure; total campus capacity is not disclosed and expansion beyond phase one is stated to depend on power availability. No grid connection agreement has been made public. Approval is being sought through Victoria's Development Facilitation Program rather than Wyndham City Council. |  |  | PGIM Real Estate's Global Data Centre Fund bought 20.7 hectares at 1 Oroya Drive, Truganina in February 2026 for about A$165.6 million, or roughly A$8 million per hectare, 22km west of the Melbourne CBD. The first of three planned phases is 80MW at a capex of about A$1.2 billion. The site sits inside the Truganina industrial cluster that already hosts AWS, Microsoft, STACK and Goodman data centre land, and PGIM has said it is in discussions on a second Melbourne site. | PGIM Real Estate 旗下 Global Data Centre Fund 于 2026 年 2 月以约 1.656亿澳元购入 1 Oroya Drive, Truganina 的 20.7 公顷用地，折合每公顷约 800万澳元，距墨尔本 CBD 以西 22 km。项目分三期，一期 80 MW，资本开支约 12亿澳元。场地处于 Truganina 工业带，周边已聚集 AWS、微软、STACK 与 Goodman 的数据中心用地。一期之后能否继续扩容取决于电力落实，满建容量未披露；审批走维州 Development Facilitation Program，不经 Wyndham City Council。PGIM 另称正在洽谈墨尔本第二宗场地。 | https://www.datacenterdynamics.com/en/news/pgim-buys-site-for-au12bn-data-center-in-melbourne-australia/ ¦ https://www.theurbandeveloper.com/articles/us-fund-manager-pgim-buys-truganina-data-centre-site ¦ https://w.media/pgim-acquires-20-7ha-melbourne-site-for-aud-1-2bn-data-centre-campus/ ¦ https://www.mingtiandi.com/real-estate/data-centres/pgim-buys-melbourne-site-for-data-centre-campus-plans-850m-first-phase/ | 2026-10-07 | IT load
macquarie-park-campus-two | Macquarie Data Centres Macquarie Park Campus Two (Talavera Road / M2) | Macquarie Data Centres | macquarie-data-centres | Macquarie Technology Group (ASX: MAQ) | NSW | Macquarie Park | Site between Talavera Road and the M2 Motorway, Macquarie Park NSW 2113 (34,200sqm; street number not disclosed) | -33.7797 | 151.1259 | Planning | Hyperscale / AI campus (carrier-neutral wholesale and colocation) | 2026 |  | 0 | 200 | 3.42 |  |  | Power for the 200MW campus is not yet secured; Macquarie points to its adjacent IC3 Super West (47MW), whose end-state power is approved and energised, as evidence of its ability to obtain Ausgrid and Transgrid capacity in Macquarie Park. Design is to use advanced air cooling in a closed loop to minimise water draw. Total development capex has not been disclosed; A$240 million is the land cost only. | Advanced air cooling, closed-loop, designed to minimise water consumption |  | Macquarie Technology Group exercised a A$240 million call option in July 2026 over a 34,200sqm parcel between Talavera Road and the M2 at Macquarie Park, adjacent to its existing IC2/IC3 campus, for a roughly 200MW engineering and data centre campus. Subdivision has completed and initial construction is guided to finish in late 2029. Designs remain subject to planning approval and customer requirements, and Macquarie has said it is exploring asset recycling and development partnerships to fund the build. The plan also includes a one-acre public park and a research and training tie-up with Macquarie University. | Macquarie Technology Group 于 2026 年 7 月行使 2.4亿澳元看涨期权，取得 Macquarie Park 内 Talavera Road 与 M2 之间 34,200 ㎡ 地块，紧邻其现有 IC2／IC3 园区，规划约 200 MW 的工程与数据中心园区。土地分割已完成，首期建设指引为 2029 年底竣工。设计仍待规划审批并按客户需求调整，建设资金来源上公司提到资产回收与开发合作两条路径；2.4亿澳元仅为地价，总资本开支未披露。电力尚未落实，公司以相邻 IC3 Super West（47 MW）满容量电力已获批并通电作为可获得 Ausgrid／Transgrid 容量的佐证。园区另规划一英亩公共绿地，并与 Macquarie University 合作做研究与技术培训。 | https://www.crn.com.au/news/2026/data-center/macquarie-unveils-plans-for-200mw-data-centre-campus-as-ai-fuels-demand ¦ https://www.datacenterdynamics.com/en/news/australias-macquarie-dc-acquires-34200-sqm-site-in-sydney-for-200mw-data-center-campus/ ¦ https://w.media/macquarie-data-centres-acquires-aud-240m-sydney-site-for-planned-200mw-ai-campus/ ¦ https://kalkine.com.au/news/announcements/macquarie-technology-group-exercises-240-million-land-option-for-new-macquarie-park-engineering-and-data-centre-campus | 2026-10-07 | IT load
nextdc-d2 | NEXTDC D2 Darwin | NEXTDC | nextdc | NEXTDC Limited (ASX: NXT) | NT | Darwin CBD | 2 Harvey Street, Darwin NT 0800 | -12.4607 | 130.8395 | Under Construction | Edge colocation (carrier-neutral), AI-ready |  |  | 0 | 6 |  |  | Google reported in NEXTDC presentations as the anchor use case via the Australia Connect / Bosun subsea cable system | Darwin CBD grid supply. Positioned as a network-edge and subsea-cable gateway serving energy, resources, defence and space workloads in northern Australia. Capex not separately disclosed within NEXTDC's group programme. |  | Uptime Institute Tier IV design target (per NEXTDC) | D2 is NEXTDC's second Darwin facility and its first at scale in the Territory, at 6MW of AI-ready capacity against D1's 1MW over 3,000sqm. The building topped out in the week of 9 March 2026 and completion is guided to the first half of FY27. NEXTDC positions D2 as a cable-landing-adjacent gateway and has indicated it will support Google's Australia Connect initiative for the Bosun subsea cable system. | D2 为 NEXTDC 在达尔文的第二座设施，也是其在北领地首个具规模的项目，AI-ready 容量 6 MW，对比 D1 的 3,000 ㎡／1 MW。主体结构于 2026 年 3 月 9 日当周封顶，交付指引为 FY27 上半年。NEXTDC 将 D2 定位为贴近海缆登陆的北部门户节点，面向能源、资源、国防与航天类负载；公司材料提到 D2 将承接 Google 的 Australia Connect 计划及 Bosun 海缆系统。设计对标 Uptime Tier IV 认证，单体资本开支未单独披露。 | https://www.datacenterdynamics.com/en/news/australias-nextdc-tops-out-6mw-data-center-in-darwin/ ¦ https://www.nextdc.com/data-centres/darwin-data-centres/d2-darwin ¦ https://www.datacentermap.com/australia/darwin/nextdc-d2-darwin/ | 2026-10-07 | IT load
cloudcarrier-shdc-moss-vale | Southern Highlands Data Campus (SHDC), Moss Vale | Cloud Carrier |  | Nakar Property / Cloud Carrier (privately Australian owned); Square Energy for on-site generation | NSW | Moss Vale (New Berrima) | 30 Douglas Road, Moss Vale NSW 2577 | -34.5103 | 150.3498 | Operational | Off-grid liquid-cooled AI/HPC campus (powered shell, carrier-neutral) | 2025 | 2026 | 15 | 300 | 67 |  |  | Grid-independent, 'diverse ultra-resilient' on-site generation rather than a network connection. Three separate gas approvals sit behind the campus: roughly 14MW already approved; roughly 16MW under DA 26/0352, refused by the Southern Regional Planning Panel on 29 June 2026 and under appeal in the NSW Land and Environment Court (2025/00448084); and approximately 673MW under SSD-102795459, at Prepare EIS with DPHI and reported as the third-largest gas plant proposed in Australia. SEARs for the 673MW application were issued in December 2025 without the usual agency consultation, an error DPHI acknowledged on 24 September 2026. | Native liquid cooling; rainwater harvesting with zero utility water draw and over a year of drought storage; target PUE below 1.2 | Australian Government Hosting Certification Framework - Certified Strategic; DB1 built to Tier III | Cloud Carrier's 67-hectare campus at 30 Douglas Road, about 6km from Moss Vale in the NSW Southern Highlands, is one of the few Australian AI campuses designed to run entirely off-grid. The first building, DB1, is a 15MW natively liquid-cooled facility described as the first of its kind commissioned in APAC and certified under the Commonwealth Hosting Certification Framework; DB2 is flagged as next. The campus is designed for several hundred megawatts, with on-site gas generation sought in three tranches, the largest of which, at about 673MW, is a State Significant Development still only at Prepare EIS and the subject of sustained local opposition and protest. | Cloud Carrier 位于新州 Southern Highlands、距 Moss Vale 约 6 km 的 30 Douglas Road 园区占地 67 公顷，是澳洲少数按完全离网设计的 AI 园区。首栋 DB1 为 15 MW 原生液冷设施，官方口径为 APAC 首座同类投运项目，并已取得联邦 Hosting Certification Framework 的 Certified Strategic 认证；DB2 已列入下一步。园区满建目标数百 MW，不接电网，改以自建燃气发电支撑，分三笔报批：约 14 MW 已获批；约 16 MW 的 DA 26/0352 于 2026 年 6 月 29 日被 Southern Regional Planning Panel 否决，现于新州土地与环境法院上诉（2025/00448084）；约 673 MW 的 SSD-102795459 由 DPHI 受理，仍处 Prepare EIS 阶段，媒体称其为澳洲第三大在批燃气电厂。该 SSD 的 SEARs 于 2025 年 12 月未经常规机构征询即发出，DPHI 已于 2026 年 9 月 24 日承认流程有误。项目面临持续的地方反对与集会。 | https://www.wsc.nsw.gov.au/Plan-and-Build/Community-Interest-Items/Southern-Highlands-Data-Campus-Power-Station-Proposal ¦ https://www.abc.net.au/news/2026-03-04/gas-plant-ai-data-centre-moss-vale/106405944 ¦ https://www.abc.net.au/news/2026-09-25/nsw-planning-admits-error-in-gas-plant-consultation/107186260 ¦ https://reneweconomy.com.au/protests-called-as-data-centre-developer-super-sizes-plans-for-fossil-gas-generation-in-southern-highlands/ ¦ https://www.datacentermap.com/australia/moss-vale/southern-highlands-data-campus-shdc/ ¦ https://www.datacentermap.com/australia/moss-vale/shdc-db1/ ¦ https://cloudcarrier.com/campus/ | 2026-10-07 | Site/grid power
cdc-hazelmere | CDC Hazelmere Campus (Perth) | CDC Data Centres | cdc | CDC Data Centres (Infratil / Commonwealth Superannuation Corporation backed) | WA | Hazelmere | Bushmead Road, Hazelmere WA 6055 | -31.9315 | 116.004 | Planning | Hyperscale campus (self-build, government and AUKUS-oriented) | 2026 |  | 0 | 192 |  |  |  | CDC states a 100% renewable supply commitment and a privately funded dedicated connection rather than relying on Western Power's shared network. Community engagement is under way with formal development applications still in preparation; site preparation and civils are expected within a year and operations from 2029. The same Hazelmere precinct saw GreenSquareDC's 120MW proposal withdrawn in May 2026 after 1,836 objections on generator noise grounds, so acoustic assessment is the live approval risk. | Closed-loop cooling with no ongoing water consumption; acoustic screening and low-glare facades proposed |  | CDC's second Western Australian campus, at Bushmead Road in Hazelmere about 15km east of the Perth CBD, is planned at 192MW and targeted to open in 2029, following its Maddington campus which is due to complete by the end of 2026. CDC has framed the Perth expansion around sovereign government, defence and AUKUS workloads. No development application had been lodged as at early October 2026; the proposal is at community engagement, and it enters a precinct where a rival 120MW application was withdrawn in May 2026 on noise grounds. | CDC 在西澳的第二个园区，位于 Perth CBD 以东约 15 km 的 Hazelmere、Bushmead Road，规划 192 MW，投运目标 2029 年；其 Maddington 园区则计划 2026 年底前完工。CDC 将此次西澳扩张与主权政府、国防及 AUKUS 类负载挂钩。公司承诺 100% 可再生电力，并自费建设专用接入，不依赖 Western Power 共享网络；冷却采用闭式循环，无持续耗水，另规划声屏障与低眩光立面。截至 2026 年 10 月初尚未正式递交规划申请，目前处社区沟通阶段。同一片区 GreenSquareDC 的 120 MW 方案已于 2026 年 5 月因 1,836 份噪声反对意见撤回，噪声评估因此是该项目最现实的审批风险。 | https://www.businessnews.com.au/article/CDC-plans-192MW-Hazelmere-data-centre ¦ https://cdc.com.au/locations/perth/hazelmere/ ¦ https://perthisok.com/news/new-hazelmere-data-centre-plans-cdc/ ¦ https://www.innovationaus.com/cdc-data-centres-heads-west-for-aukus-boom/ | 2026-10-07 | IT load
greensquaredc-mel1-spotswood | GreenSquareDC MEL1 Spotswood (44-76 Simcock Avenue) | GreenSquareDC | greensquaredc | GreenSquareDC | VIC | Spotswood | 44-76 Simcock Avenue, Spotswood VIC 3015 | -37.8278 | 144.88 | Planning | Hyperscale / AI campus (wholesale) | 2026 |  | 0 | 240 |  |  |  | Grid supply and connection capacity not disclosed. The permit is being assessed under Victoria's Development Facilitation Program, so the Planning Minister rather than Hobsons Bay City Council is the responsible authority; this removes council refusal risk but concentrates the decision politically. Victoria's Sustainable Data Centre Action Plan of September 2026, with its 150m residential buffer and own-renewable-supply rule, applies directly to an inner-west site of this kind. |  |  | GreenSquareDC has applied for a 240MW data centre at 44-76 Simcock Avenue, Spotswood, roughly 7km west of the Melbourne CBD, under permit application PA2604553 described as 'use and development of the land for a utility installation (data centre)'. The application has been under assessment through Victoria's Development Facilitation Program since 31 July 2026, with the company targeting live status around 2027. A dedicated residents' campaign is running against the proposal, and the site's inner-urban location makes it a direct test of the buffer and renewable-supply rules Victoria proposed in September 2026. | GreenSquareDC 就 44-76 Simcock Avenue, Spotswood 递交 240 MW 数据中心许可申请（PA2604553，事由为 utility installation 用途及开发），场地距墨尔本 CBD 以西约 7 km。申请自 2026 年 7 月 31 日起由维州 Development Facilitation Program 评估，责任机构为规划部长而非 Hobsons Bay City Council，公司目标 2027 年前后投运。电网供电与接入容量未披露。项目已出现有组织的居民反对。场地属内城区，正面撞上维州 2026 年 9 月提出的 150 m 住宅缓冲与自备可再生电力要求，是该套新规的第一批实际检验对象。 | https://nodatacentreinspotswood.com/ ¦ https://datacenterhawk.com/marketplace/providers/greensquaredc/50-simcock-avenue/mel1 ¦ https://www.abc.net.au/news/2026-09-22/victorian-data-centres-policy-renewable-energy-mandates/107178138 | 2026-10-07 | IT load
greensquaredc-hazelmere | GreenSquareDC Hazelmere Data Centre (withdrawn) | GreenSquareDC | greensquaredc | GreenSquareDC (applicant); landowner not confirmed | WA | Hazelmere | Stirling Crescent, Hazelmere WA 6055 | -31.9268 | 116.0005 | Withdrawn | Wholesale / AI campus (withdrawn application) | 2025 |  | 0 | 120 | 4.5 | 600 |  | Application withdrawn on 14 May 2026, five days before the scheduled Metro Inner-South Joint Development Assessment Panel hearing. City of Swan planning staff had recommended refusal because modelled noise from standby diesel generators in an emergency scenario exceeded acceptable levels at nearby receivers. 1,836 of 1,897 submissions objected, citing noise, heat, electromagnetic energy and exhaust, with additional concerns over proximity to the Helena River Steiner School, Aboriginal heritage and a conservation wetland. No resubmission or alternative Perth site has been announced. |  |  | GreenSquareDC's 120MW, roughly A$600 million proposal on 4.5 hectares at Stirling Crescent, Hazelmere, about 15km east of Perth, was withdrawn on 14 May 2026 after attracting 1,836 objections from 1,897 submissions and a refusal recommendation from City of Swan planners over standby generator noise. The record is retained because the refusal is the clearest Australian precedent to date for acoustic assessment defeating a large data centre application, and because CDC has since proposed a 192MW campus in the same precinct. | GreenSquareDC 位于 Perth 以东约 15 km、Hazelmere 的 Stirling Crescent 项目占地 4.5 公顷，规划 120 MW，投资约 6亿澳元，于 2026 年 5 月 14 日撤回申请，距 Metro Inner-South JDAP 听证仅五天。City of Swan 规划部门此前建议否决，理由是应急工况下备用柴发的噪声模型在邻近敏感点超标；1,897 份意见中 1,836 份反对，集中在噪声、排热、电磁与尾气，另涉及紧邻 Helena River Steiner School、原住民遗产点与一处保护湿地。公司未宣布重新申报或改址。保留该条记录有两个理由：这是迄今澳洲最清晰的一例——噪声评估直接击落大型数据中心申请——且 CDC 随后在同一片区提出 192 MW 方案。 | https://mlq.ai/news/v2/greensquaredc-withdraws-120mw-perth-data-center-application-after-1836-objections/ ¦ https://echonewspaper.com.au/news/hazelmere-data-centre-application-withdrawn/ ¦ https://www.theurbandeveloper.com/articles/greensquaredc-data-centre-hazelmere-perth-wa-public-comment | 2026-10-07 | IT load
digital-realty-syd13-waterloo-rd | Digital Realty SYD13 Redevelopment, Macquarie Park (23-25 Waterloo Road) | Digital Realty | digital-realty | Digital Realty Trust | NSW | Macquarie Park / North Ryde | 23-25 Waterloo Road, Macquarie Park NSW 2113 | -33.788 | 151.123 | Planning | Colocation and interconnection (carrier-neutral), multi-storey redevelopment | 2026 |  |  | 70 | 1.2 | 700 |  | 70MW on a 1.2-hectare inner-metropolitan site implies a dedicated high-voltage supply well beyond the existing building's draw; no Ausgrid or Transgrid connection agreement has been made public. The existing single-storey SYD13, originally built for Exodus Communications, would be demolished. Operating IT load of the existing building is not disclosed. |  |  | Digital Realty lodged a SEARs application with the NSW Department of Planning in April 2026 to demolish its existing single-storey SYD13 facility at 23-25 Waterloo Road, Macquarie Park and replace it with a 23,375sqm, eight-storey, 70MW data centre representing up to A$700 million of investment. It is one of the larger brownfield densification plays in the Macquarie Park cluster, where Goodman, Stockland, Macquarie Data Centres and ISPT are all building or proposing capacity. | Digital Realty 于 2026 年 4 月向新州规划部门递交 SEARs 申请，拟拆除 23-25 Waterloo Road, Macquarie Park 现有单层 SYD13 设施，改建 23,375 ㎡、八层、70 MW 的数据中心，投资规模最高 7亿澳元。现有建筑原为 Exodus Communications 所建，其在运 IT负载未披露。1.2 公顷内城用地做 70 MW，意味着需要远超现状的专用高压供电，Ausgrid／Transgrid 接入协议尚未公开。该项目是 Macquarie Park 集群中规模较大的棕地加密案例，同片区 Goodman、Stockland、Macquarie Data Centres 与 ISPT 均在建或在报新增容量。 | https://www.datacenterdynamics.com/en/news/former-exodus-data-center-in-sydney-australia-to-be-replaced-with-70mw-facility/ ¦ https://baxtel.com/news/a-70mw-facility-is-set-to-replace-the-former-exodus-data-center-in-sydney-australia ¦ https://www.datacentermap.com/australia/sydney/23-waterloo-rd-syd12/ | 2026-10-07 | IT load
keppel-gore-hill | Keppel Gore Hill Data Centre & Keppel DC Sydney 1, Artarmon | Keppel Data Centres |  | Keppel DC REIT | NSW | Artarmon (Gore Hill Technology Park) | 5 Broadcast Way, Artarmon NSW 2064 | -33.8195 | 151.183 | Operational | Colocation (carrier-neutral), Tier III |  | 2011 | [5 empty] | Power capacity is not disclosed by Keppel DC REIT at asset level. Keppel acquired an adjacent 3,840sqm freehold plot in August 2019 for Keppel DC Sydney 1 (KDC SY 1), a three-phase greenfield build of about 57,000 square feet GFA to Tier III equivalent specification, with phase one shell, core and initial fit-out completed in the first half of 2021. |  | Tier III (purpose-built four-storey facility) | Keppel's only operating Australian data centre asset is at Gore Hill Technology Park, roughly 9km north-west of the Sydney CBD: a four-storey purpose-built Tier III facility held by Keppel DC REIT, operating since 2011, with multiple carrier networks on site. Keppel added the adjacent KDC SY 1 development in 2019. The record matters to the index because it establishes Keppel as an incumbent Australian operator rather than a new entrant, ahead of its 720MW Morwell campus. | Keppel 在澳洲唯一在运的数据中心资产位于悉尼 CBD 西北约 9 km 的 Gore Hill Technology Park，为 Keppel DC REIT 持有的四层定制 Tier III 设施，2011 年起运营，场内接入多家运营商网络。2019 年 8 月 Keppel 另购入相邻 3,840 ㎡ 永久产权地块开发 Keppel DC Sydney 1（KDC SY 1），分三期建设、GFA 约 57,000 平方英尺，按 Tier III 等效标准设计，一期外壳与初始装修于 2021 年上半年完成。资产层面的电力容量未披露。该条记录的意义在于确认 Keppel 是澳洲既有运营商而非新进入者，其 720 MW 的 Morwell 园区是在此基础上的扩张。 | https://www.keppeldatacentres.com/locations/asia-pacific/australia/gore-hill-data-centre/ ¦ https://baxtel.com/data-center/keppel-sydney-gore-hill ¦ https://www.keppel.com/media/keppel-expands-data-centre-footprint-in-sydney-australia-6763/ | 2026-10-07 | IT load
equinix-me1-me2-port-melbourne | Equinix ME1 / ME2 Port Melbourne | Equinix | equinix | Equinix, Inc. | VIC | Port Melbourne | 552-578 Lorimer Street, Port Melbourne VIC 3207 | -37.8265 | 144.9185 | Operational | Carrier-neutral colocation and interconnection (IBX) |  | 2015 | [5 empty] | Equinix does not disclose IBX-level power capacity for its Melbourne sites. ME1 and ME2 sit on the same Lorimer Street holding and are physically bridged, so they function as one interconnection campus. Equinix also operates ME4 at Derrimut, recorded separately in this index, and ME5 in Melbourne. |  |  | ME1 opened in March 2015 as Equinix's first purpose-built Melbourne International Business Exchange and remains, with the adjoining ME2, the city's principal carrier-neutral interconnection point. The two buildings are adjacent on Lorimer Street in Port Melbourne and are connected, with ME2 carrying the wider interconnection fabric. The index previously recorded only ME4 Derrimut for Equinix in Victoria, which understated Equinix's position in the Melbourne peering market. | ME1 于 2015 年 3 月投运，是 Equinix 在墨尔本首座定制 IBX；与紧邻的 ME2 共同构成本地最主要的运营商中立互联节点。两栋建筑同处 Port Melbourne 的 Lorimer Street 地块并以连廊相通，ME2 承载更完整的互联结构。Equinix 不按设施披露电力容量。此前索引在维州仅收录 Equinix ME4 Derrimut，低估了其在墨尔本 peering 市场的地位；Equinix 在墨尔本另有 ME5。 | https://newsroom.equinix.com/2015-03-23-Equinix-Connects-Melbourne-with-New-International-Business-Exchange-Data-Center,1 ¦ https://www.datacentermap.com/australia/melbourne/equinix-me1/ ¦ https://www.equinix.com/data-centers/asia-pacific-colocation/australia-colocation/melbourne-data-centers | 2026-10-07 | IT load
adc-mitchell-canberra | Australian Data Centres Mitchell (Canberra) | Australian Data Centres (ADC) |  | Australian Data Centres | ACT | Mitchell | 38 Vicars Street, Mitchell ACT 2911 | -35.2213 | 149.1335 | Operational | Colocation (carrier-neutral), government-certified |  | 2014 |  |  |  |  | Australian Government agencies (Hosting Certification Framework Certified Strategic workloads) | Power capacity not disclosed. Electrical topology is 2N with five Eurodiesel 2.25 MVA diesel-rotary UPS units, supporting rack densities to 33kW. ADC also acquired Verizon's 105 Gladstone Street, Fyshwick facility in December 2025, originally built around 2009, and has a capital works programme under way to uplift its capacity. |  | Australian Government Hosting Certification Framework - Certified Strategic | ADC is the main Canberra colocation operator outside CDC, Equinix, Macquarie, NEXTDC and STACK, and its Mitchell facility has been operational since 2014 on a 2N electrical design using diesel-rotary UPS, with rack densities to 33kW. ADC expanded in December 2025 by acquiring Verizon's long-running Fyshwick site, which it has integrated and certified. Its scale is modest but its Certified Strategic status makes it structurally relevant to the sovereign government hosting market the ACT cluster exists to serve. | 在 CDC、Equinix、Macquarie、NEXTDC 与 STACK 之外，ADC 是堪培拉主要的托管运营商。其 Mitchell 设施 2014 年投运，电气为 2N 架构，配五台 Eurodiesel 2.25 MVA 柴油旋转式 UPS，单柜功率可至 33 kW；电力容量未披露。2025 年 12 月 ADC 收购 Verizon 运营逾十五年的 Fyshwick 站点（约 2009 年建成），已完成整合并取得认证，同时启动扩容的资本工程。ADC 体量不大，但持有 Hosting Certification Framework 的 Certified Strategic 资质，对首都领地集群所服务的主权政府托管市场具有结构性意义。 | https://baxtel.com/data-center/adc-mitchell ¦ https://www.datacenterdynamics.com/en/news/australian-data-centres-acquires-campus-in-canberra/ | 2026-10-07 | IT load
nextdc-sc1 | NEXTDC SC1 Sunshine Coast | NEXTDC | nextdc | NEXTDC Limited (ASX: NXT) | QLD | Maroochydore (Sunshine Coast) | 44 Maud Street, Maroochydore QLD 4558 | -26.6565 | 153.0905 | Operational | Edge colocation (carrier-neutral), cable-landing adjacent |  | 2021 | 1 |  |  |  |  | Grid supply via Energex. The facility's value is interconnection rather than capacity: direct access to the Sunshine Coast international broadband cable landing station gives the shortest east-coast route into Asia, which is the rationale for the adjoining SC2 build already recorded in this index. |  |  | SC1 opened on 8 December 2021 at 44 Maud Street, Maroochydore with about 1MW of capacity, as the anchor colocation facility for the Sunshine Coast international broadband cable landing station. It is small, but it is the landing-side counterpart to NEXTDC SC2 and the only carrier-neutral facility with direct access to that cable, which gives the Sunshine Coast its only genuine claim on Asia-facing latency. | SC1 于 2021 年 12 月 8 日在 44 Maud Street, Maroochydore 投运，容量约 1 MW，是 Sunshine Coast 国际海缆登陆站的锚定托管设施。规模虽小，但它是本索引已收录的 NEXTDC SC2 的登陆侧对应设施，也是唯一可直连该海缆的运营商中立站点，构成 Sunshine Coast 在亚洲方向时延上的全部实质优势。供电由 Energex 提供。 | https://www.datacentermap.com/australia/sunshine-coast/nextdc-sc1/ ¦ https://www.nextdc.com/data-centres | 2026-10-07 | IT load
resetdata-aif1-docklands | ResetData AI Factory AI-F1, Docklands | ResetData | centuria-resetdata | ResetData, in partnership with Centuria Capital Group | VIC | Docklands (Melbourne) | 818 Bourke Street, Docklands VIC 3008 | -37.8203 | 144.946 | Operational | Sovereign AI factory (GPU-as-a-service), liquid immersion | 2025 | 2025 | 1.25 | 1.5 |  |  |  | Retrofit inside an existing Docklands commercial building rather than a purpose-built shell, which is the point: immersion cooling lets high-density GPU racks run on a base-building electrical and mechanical envelope. Centuria has separately secured A$165 million of GPU debt and 72MW of power for its sovereign AI pipeline, of which AI-F1 is the first deployment. | Single-phase liquid immersion; no wastewater, around 45% lower emissions claimed versus conventional air cooling |  | AI-F1 went live on 25 August 2025 at 818 Bourke Street, Docklands as Australia's first commercial immersion-cooled AI factory, with 1.25MW of initial NVIDIA deployment inside a 1.5MW envelope, delivered with Centuria Capital Group. It is tiny by campus standards and is included because it is the reference case for retrofitting dense AI compute into existing commercial buildings, a model being pitched to Australian landlords as an alternative to greenfield capacity. | AI-F1 于 2025 年 8 月 25 日在 818 Bourke Street, Docklands 投运，为澳洲首个商用浸没式液冷 AI 工厂，与 Centuria Capital Group 合作交付，1.5 MW 容量内首批部署 NVIDIA 设备 1.25 MW。按园区口径体量极小，收录原因在于它是在既有商业楼宇内改造高密度 AI 算力的样板：浸没冷却使高密度 GPU 机柜可在base-building 的电气与暖通条件下运行，这一模式正被推介给澳洲业主作为新建产能之外的替代路径。Centuria 另已为其主权 AI 管线锁定 1.65亿澳元 GPU 债务融资与 72 MW 电力，AI-F1 是其中首个落地项目。 | https://www.datacentermap.com/australia/melbourne/resetdata-ai-factory-ai-f1/ ¦ https://www.datacenterdynamics.com/en/news/resetdata-and-centuria-capital-group-launch-nvidia-powered-ai-factory-and-marketplace-in-melbourne-australia/ | 2026-10-07 | IT load
macquarie-ic1-sydney | Macquarie Data Centres IC1 Sydney CBD | Macquarie Data Centres | macquarie-data-centres | Macquarie Technology Group (ASX: MAQ) | NSW | Sydney CBD | 477 Pitt Street, Sydney NSW 2000 | -33.881 | 151.207 | Operational | Colocation (carrier-neutral), CBD edge |  |  | 3 |  |  |  |  | CBD grid supply via Ausgrid. IC1 is the legacy Sydney CBD node of the Macquarie estate, serving latency-sensitive and financial-sector racks; growth capacity sits at Macquarie Park (IC2, IC3, IC3 Super West and the planned 200MW Campus Two) rather than here. |  |  | IC1 is Macquarie Data Centres' 3MW Sydney CBD colocation facility at 477 Pitt Street, offering racks and dedicated whitespace under a 99.98% service level guarantee. It is small and operationally static, but it completes the Macquarie estate in the index alongside IC2 and IC3 at Macquarie Park, the IC4/IC5 Canberra bunker campus and the newly acquired 200MW Macquarie Park site. | IC1 是 Macquarie Data Centres 在悉尼 CBD 的 3 MW 托管设施，位于 477 Pitt Street，提供机柜与独立白空间，SLA 为 99.98%。该站点规模小、运营上也基本稳定，增量容量集中在 Macquarie Park（IC2、IC3、IC3 Super West 及新购的 200 MW Campus Two）。收录目的是补齐索引中 Macquarie 资产组合——与 Macquarie Park 的 IC2／IC3、堪培拉 IC4／IC5 地堡园区并列。供电由 Ausgrid 经 CBD 网络提供。 | https://www.datacentermap.com/australia/sydney/intellicentre-1/ | 2026-10-07 | IT load

## Operators
operator_id | name | legal_name | name_zh | category | hq_country | hq_city | founded_year | ownership_type | key_shareholders | ticker | au_operational_mw | au_pipeline_mw | au_facility_count | announced_investment_aud_bn | key_customers | background_en | background_zh | website | sources | last_verified
airtrunk | AirTrunk | AirTrunk | AirTrunk | Colocation/Wholesale | Australia | Sydney | 2015 | Private (PE) | Blackstone (Real Estate & Infrastructure funds) and CPP Investments (~12%), acquired Sept 2024 for A$24bn implied EV from Macquarie Asset Management / PSP Investments |  |  | 2400 | 5 | 12 | Microsoft, AWS, Google, Meta, Oracle (hyperscale wholesale; customers not formally disclosed) | AirTrunk is the largest hyperscale wholesale data centre platform in Australia and APAC. - Founded in Sydney in 2015 by Robin Khuda; bought by Blackstone and CPP Investments in September 2024 for A$24bn. - Pure wholesale model: sells multi-hall capacity to the global cloud providers. - Five Australian campuses (SYD1 121MW+, SYD2 158MW+, SYD3 330MW+, MEL1 276MW+, MEL2 354MW+) totalling 1.2GW+ operating and planned. - Kemps Creek 1.2GW under NSW assessment; a 540MW, A$3.7bn Kurri Kurri SSD was lodged in September 2026 on the former Hydro Aluminium smelter site, with a A$37m community package. - The ~US$1.5bn Singapore REIT of stabilised assets was still unlaunched as at 7 October 2026. | AirTrunk是澳洲及亚太最大的超大规模批发型数据中心平台。 - 2015年由Robin Khuda在悉尼创立；2024年9月Blackstone与CPP Investments以240亿澳元收购。 - 纯批发模式，向全球云厂商整栋出租机房。 - 澳洲五个园区（SYD1 121MW+、SYD2 158MW+、SYD3 330MW+、MEL1 276MW+、MEL2 354MW+），在运及规划容量超1.2GW。 - Kemps Creek 1.2GW待新州审批；2026年9月在Kurri Kurri原Hydro Aluminium冶炼厂地块申报540MW、37亿澳元州重大项目，配套3700万澳元社区方案。 - 约15亿美元的新加坡REIT至2026年10月7日仍未启动发行。 | https://airtrunk.com | https://airtrunk.com/airtrunk-expands-australian-platform-with-a-second-hyperscale-data-centre-campus-in-melbourne/ ¦ https://www.blackstone.com/news/press/blackstone-announces-agreement-to-acquire-airtrunk-in-a-a24b-transaction/ ¦ https://www.realestatesource.com.au/blackstone-weighs-airtrunk-asset-spin-off/ ¦ https://ia.acs.org.au/article/2026/concern-over-australia-s-most-power-hungry-data-centre.html ¦ https://bebeez.eu/2025/11/11/airtrunk-set-to-buy-planned-1gw-data-center-site-in-western-sydney-australia/ ¦ https://en.wikipedia.org/wiki/AirTrunk | 2026-10-07
nextdc | NEXTDC | NEXTDC | NEXTDC | Colocation/Wholesale | Australia | Brisbane | 2010 | ASX-listed | Widely held; institutional register (Vanguard, State Street, AustralianSuper and other index/super funds); A$1.5bn entitlement offer May 2026 | ASX:NXT | 288 | 537 | 17 | 9.75 | Microsoft, AWS, Google, Oracle, OpenAI (S7 MoU), IBM, Telstra, NBN, Australian government agencies; Cloud & AI = 68% of contracted MW | NEXTDC is Australia's largest ASX-listed pure-play data centre operator. - Founded in Brisbane in 2010 by Bevan Slattery and listed on the ASX the same year. - Tier III/IV colocation and hyperscale network across eight Australian cities plus Kuala Lumpur, Tokyo and Auckland. - Planned group IT capacity 1.8GW+ (land bank 3GW+), anchored by S4 (350MW), S7 (612MW, OpenAI anchor) and the A$2bn, 150MW M4 AI factory at Port Melbourne. - FY26 contracted utilisation 740MW, 288MW built and 537MW under construction. - Raised A$1.1bn of convertible notes in September 2026, its third capital raise in four months; CEO Craig Scroggie chairs the new Data Centres Australia peak body. | NEXTDC是ASX最大的上市纯数据中心运营商。 - 2010年由Bevan Slattery在布里斯班创立，同年在ASX上市。 - 在澳洲八个城市运营Tier III/IV托管与超大规模设施，吉隆坡、东京、奥克兰在建。 - 集团规划IT容量超1.8GW（土地储备超3GW），核心为S4（350MW）、S7（612MW，OpenAI为锁定租户）及墨尔本Port Melbourne的M4 AI工厂（20亿澳元、150MW）。 - FY26签约容量740MW，已建成288MW，在建537MW。 - 2026年9月发行11亿澳元可转债，为四个月内第三次融资；CEO Craig Scroggie出任新成立行业组织Data Centres Australia主席。 | https://www.nextdc.com | https://www.investing.com/news/company-news/nextdc-fy26-presentation-740mw-contracted-revenue-to-jump-50-93CH-4880417 ¦ https://www.nextdc.com/hubfs/ASX%20Announcements/1H26%20Results%20Presentation.pdf ¦ https://www.nextdc.com/news/record-contracted-growth-and-a2.2bn-capital-plan-to-scale-ai-ready-infrastructure ¦ https://www.datacenterdynamics.com/en/news/australian-stargate-data-center-in-sydney-will-offer-612mw-of-capacity/ ¦ https://announcements.asx.com.au/asxpdf/20260420/pdf/06ymvmm97tvsh4.pdf | 2026-10-07
cdc | CDC Data Centres | CDC Data Centres | CDC Data Centres | Government-focused | Australia | Canberra | 2007 | Private | Infratil 49.69% (NZX/ASX: IFT), Future Fund 34.5%, Commonwealth Superannuation Corporation 12.0%, CDC management (post Feb-2025 CSC sell-down); independently valued at A$18.5bn midpoint (range A$17.4-19.6bn) at 30 September 2026 |  | 550 | 810 |  | 4 | Australian Government (Defence, ASD, ATO, Home Affairs), NZ Government, Microsoft, AWS, unnamed US investment-grade hyperscaler (555MW, 30-year), ResetData; the Firmus relationship was wound back to 42MW in October 2026 | CDC Data Centres is Australia's dominant sovereign/government-certified operator, now pivoting hard into hyperscale. - Founded in 2007 by Greg Boorer to host classified Australian Government workloads; owned by Infratil (49.69%), the Future Fund and CSC. - Nine operating Australian campuses across Sydney, Melbourne, Canberra and Perth, plus two in Auckland and the 250MW Stratford JV with Contact Energy. - September 2026 investor day: 1.1GW contracted (625MW signed since May 2026), 350MW deployed and earning, 810MW under construction across FY27-29, 3.9GW leasable pipeline. - FY27 guidance lifted to A$710-750m EBITDAF on A$3.8-4.2bn of capex (ex-land); FY28 targeted above A$1bn, with over A$1bn of land purchases settling across FY27-28. - In the window it won approval for the 84MW, A$203.5m Beard 2 in Canberra, lodged a 1.4GW, A$15bn Wagga Wagga campus, and ended the 1.6GW Firmus Southgate tie-up after only 42MW. | CDC Data Centres是澳洲主权级/政府认证数据中心龙头，近年全面转向超大规模。 - 2007年由Greg Boorer创立，起点是承载联邦政府涉密系统；股东为Infratil（49.69%）、Future Fund和CSC。 - 澳洲在运九个园区，分布于悉尼、墨尔本、堪培拉、珀斯；另有奥克兰两处及与Contact Energy合资的250MW Stratford项目。 - 2026年9月投资者日：签约1.1GW（5月以来新签625MW）、已投产并产生收入350MW、在建810MW（FY27-29交付）、可租管线3.9GW。 - FY27 EBITDAF指引上调至7.1-7.5亿澳元，资本开支38-42亿澳元（不含土地）；FY28目标超10亿澳元，FY27-28还有逾10亿澳元土地款交割。 - 本窗口内获批堪培拉Beard 2（84MW、2.035亿澳元），申报Wagga Wagga 1.4GW、150亿澳元园区，并终止与Firmus的1.6GW Southgate合作，实际仅落地42MW。 | https://www.cdcdatacentres.com.au | https://www.sharecafe.com.au/2026/07/06/infratils-cdc-valuation-soars-to-a18-5-billion-on-capacity-growth/ ¦ https://infratil.com/news/cdc-signs-555mw-data-centre-contract-with-us-customer/cdc-signs-555mw-data-centre-contract-with-us-customer/ ¦ https://www.datacenterdynamics.com/en/news/cdc-signs-largest-ever-aussie-data-center-deal-to-provide-555mw-for-us-client/ ¦ https://www.mingtiandi.com/real-estate/data-centres/australias-cdc-lands-record-555mw-ai-data-centre-deal-with-us-client/ ¦ https://www.futurefund.gov.au/news-room/Future-Fund-acquires-further-shares-in-CDC ¦ https://infratil.com/news/cdc-independent-valuation-31-march-2026/ | 2026-10-07
infratil | Infratil | Infratil | Infratil | Developer/Investor | New Zealand | Wellington | 1994 | ASX-listed | Widely held NZX/ASX dual listing; managed by Morrison (formerly H.R.L. Morrison & Co) | NZX:IFT / ASX:IFT |  |  |  |  | n/a (investor) - underlying CDC customers: Australian Government, hyperscalers | Infratil is the most liquid listed proxy for CDC Data Centres' government and hyperscale growth. - Wellington-based infrastructure investor listed on NZX/ASX, managed by Morrison. - Largest asset is a 49.69% stake in CDC, alongside One NZ, Longroad Energy and other renewables platforms. - CDC independently valued at A$18.5bn midpoint (range A$17.4-19.6bn) at 30 September 2026; the Infratil stake is A$9.168bn, down A$45m on the quarter from A$9.213bn. - Stronger contracting and pipeline were offset by a higher forward yield curve lifting assumed interest costs, ending a run of upward CDC revaluations. - CDC's September investor day lifted FY27 EBITDAF guidance to A$710-750m and reaffirmed above A$1bn for FY28. | Infratil是分享CDC政府及超大规模业务增长流动性最好的上市标的。 - 总部惠灵顿，NZX/ASX双重上市，由Morrison管理。 - 最大资产为CDC 49.69%股权，另持有One NZ、Longroad Energy等可再生能源平台。 - 2026年9月30日CDC独立估值中值185亿澳元（区间174-196亿澳元）；Infratil所持股权91.68亿澳元，较上季的92.13亿澳元下降4500万澳元。 - 签约量与管线改善被远期收益率曲线上行抬高的融资成本假设抵消，CDC连续上调估值的势头就此中断。 - CDC 9月投资者日将FY27 EBITDAF指引上调至7.1-7.5亿澳元，并重申FY28超10亿澳元。 | https://infratil.com | https://www.sharecafe.com.au/2026/07/06/infratils-cdc-valuation-soars-to-a18-5-billion-on-capacity-growth/ ¦ https://infratil.com/news/infratil-full-year-results-for-the-year-ended-31-march-2026/infratil-fy2026-full-year-result-media-release/ ¦ https://infratil.com/news/cdc-independent-valuation-31-march-2026/ | 2026-10-07
equinix | Equinix | Equinix Australia | Equinix | Colocation/Wholesale | United States | Redwood City (AU HQ Sydney) | 1998 | Subsidiary of listed parent | Equinix Inc. (NASDAQ: EQIX); xScale Australia JV 80% PGIM Real Estate / 20% Equinix | NASDAQ:EQIX |  |  | 18 | 1.1 | AWS, Microsoft, Google, Oracle, Telstra, Optus, banks and enterprises; 2,000+ networks via Equinix Fabric | Equinix is Australia's leading retail/interconnection colocation provider and network hub. - Entered Australia in 2002 via Pihana Pacific. - 18 IBX data centres: eight in Sydney, four in Melbourne, three in Perth, one each in Brisbane, Canberra and Adelaide; ~68,000 sqm of colocation space. - Hosts the major cloud on-ramps and subsea cable landings. - Hyperscale capacity via the xScale JV with PGIM Real Estate (SY9x Rosehill); parent does not disclose Australian MW. | Equinix是澳洲零售托管与互联生态的领导者，也是核心网络枢纽。 - 2002年通过收购Pihana Pacific进入澳洲。 - 18座IBX：悉尼8座、墨尔本4座、珀斯3座，布里斯班、堪培拉、阿德莱德各1座；托管面积约6.8万平方米。 - 承载主要云接入节点和海缆登陆站。 - 超大规模业务通过与PGIM Real Estate合资的xScale推进（Rosehill SY9x）；母公司不披露澳洲MW。 | https://www.equinix.com/data-centers/asia-pacific-colocation/australia-colocation | https://www.equinix.com/data-centers/asia-pacific-colocation/australia-colocation ¦ https://newsroom.equinix.com/press-releases?item=125027 ¦ https://investor.equinix.com/news-events/press-releases/detail/964/equinix-and-pgim-real-estate-open-first-xscale-data ¦ https://newsroom.equinix.com/2025-09-22-Equinix-Selected-for-SMAP-Cable-Landing-in-Perth-and-Sydney | 2026-09-15
digico | DigiCo Infrastructure REIT | DigiCo Infrastructure REIT (incl. Global Switch Sydney, iseek, YourDC) | DigiCo REIT (Global Switch Sydney / iseek / YourDC) | Colocation/Wholesale | Australia | Sydney | 2024 | ASX-listed | Externally managed by HMC Capital (ASX: HMC), which holds a cornerstone stake; A$2.4bn IPO Dec 2024 | ASX:DGT |  | 88 | 6 | 2.12 | Australian Government agencies (SYD1 Certified Strategic), Telstra, Optus, Vocus, cloud & enterprise tenants; Queensland Government (iseek); Defence/SA Government (YourDC) | DigiCo Infrastructure REIT is the first ASX-listed data centre REIT, externally managed by HMC Capital. - Created by HMC Capital; listed December 2024 via a A$2.4bn IPO, the largest Australian float that year. - Australian portfolio: former Global Switch Sydney campus at Ultimo (SYD1, 120MVA allocated, Certified Strategic), iseek in Brisbane and Townsville, YourDC's two Adelaide sites. - US assets in Dallas, Kansas City and Los Angeles after the Chicago sale. - Group planned IT capacity ~238MW; billed capacity targeted at 85MW+ from July 2026. - The 88MW SYD1 expansion is the key growth project. | DigiCo Infrastructure REIT是ASX首只数据中心REIT，由HMC Capital外部管理。 - HMC Capital组建，2024年12月以24亿澳元IPO上市，为当年澳洲最大IPO。 - 澳洲资产：原Global Switch悉尼Ultimo园区（SYD1，已分配120MVA，Certified Strategic认证）、iseek布里斯班及Townsville设施、YourDC阿德莱德两站。 - 出售芝加哥后，美国保留Dallas、Kansas City、Los Angeles资产。 - 集团规划IT容量约238MW，2026年7月起计费容量目标85MW以上。 - SYD1 88MW扩建是核心增长项目。 | https://www.digi-co.com.au | https://www.hmccapital.com.au/investment-strategies/digital-infrastructure/digico-infrastructure-reit/asx-announcements/digico-announces-customer-wins-provides-earnings-guidance/ ¦ https://www.hmccapital.com.au/investment-strategies/digital-infrastructure/digico-infrastructure-reit/asx-announcements/fy25-results-announcement/ ¦ https://www.datacenterdynamics.com/en/news/australias-digico-infrastructure-reit-signs-14mw-of-data-center-deals/ ¦ https://www.sharecafe.com.au/2026/05/06/digico-infrastructure-reit-fortifies-balance-sheet-with-us750m-asset-sale/ ¦ https://www.fool.com.au/2026/08/21/digico-infrastructure-reit-posts-fy26-earnings-beat-outlines-expansion-plans/ ¦ https://www.globalswitch.com/announcement/agreement-reached-for-the-sale-of-global-switch-australia-to-hmc-capital/ | 2026-09-15
hmc-capital | HMC Capital | HMC Capital | HMC Capital | Developer/Investor | Australia | Sydney | 2019 | ASX-listed | Founder/CEO David Di Pilla and management, institutional holders | ASX:HMC |  |  |  |  | n/a (fund manager) - manages DigiCo Infrastructure REIT and unlisted digital infrastructure funds | HMC Capital is the Sydney-based alternative asset manager behind DigiCo Infrastructure REIT. - Founded by David Di Pilla in 2019. - Built a digital infrastructure platform in 2024 by acquiring Global Switch Australia (A$2.12bn), iseek and YourDC, then floated them as DigiCo. - Earns management and performance fees as DigiCo's external manager; the vehicle that gave Australian investors the first ASX-listed data centre REIT. - Watch-points: execution of the SYD1 expansion and recycling of US assets. | HMC Capital是DigiCo Infrastructure REIT背后的悉尼另类资产管理公司。 - 2019年由David Di Pilla创立。 - 2024年收购Global Switch澳洲（21.2亿澳元）、iseek和YourDC搭建数字基础设施平台，并打包为DigiCo上市。 - 作为DigiCo外部管理人收取管理费与业绩报酬；澳洲首只上市数据中心REIT的推手。 - 观察点：SYD1扩建执行进度、美国资产回收。 | https://www.hmccapital.com.au | https://www.hmccapital.com.au/investment-strategies/digital-infrastructure/digico-infrastructure-reit/asx-announcements/digico-announces-customer-wins-provides-earnings-guidance/ ¦ https://www.globalswitch.com/announcement/agreement-reached-for-the-sale-of-global-switch-australia-to-hmc-capital/ ¦ https://www.datacenterdynamics.com/en/news/australias-digico-infrastructure-reit-signs-14mw-of-data-center-deals/ | 2026-09-15
macquarie-data-centres | Macquarie Data Centres | Macquarie Data Centres (Macquarie Technology Group) | Macquarie Data Centres | Government-focused | Australia | Sydney | 1992 | ASX-listed | Founders David and Aidan Tudehope (~50%+), institutional holders; National Reconstruction Fund Corporation invested A$200m (IC3 Super West) | ASX:MAQ |  | 47 | 6 | 0.35 | Australian Government (42% of federal agencies), Defence, hyperscale/AI anchor customer under negotiation, enterprise & telco | Macquarie Data Centres is the sovereign data centre arm of ASX-listed Macquarie Technology Group. - Parent (formerly Macquarie Telecom) founded in 1992 by David and Aidan Tudehope; the only ASX-listed telco-turned-sovereign DC operator. - Macquarie Park campus in Sydney (IC1, IC2, IC3 East, new 47MW IC3 Super West; scalable to ~200MW) plus IC4 and IC5 in Canberra. - Positioned as 'Australia's sovereign home of AI' for government and regulated workloads; government hosting is the highest-margin segment. - IC3 Super West opening in late 2026 is the growth inflection. | Macquarie Data Centres是ASX上市Macquarie Technology Group旗下的主权数据中心业务。 - 母公司（原Macquarie Telecom）1992年由David与Aidan Tudehope创立，是ASX唯一由电信商转型的主权数据中心运营商。 - 悉尼Macquarie Park园区（IC1、IC2、IC3 East及新建47MW IC3 Super West，可扩至约200MW），另有堪培拉IC4、IC5。 - 定位'澳洲主权AI之家'，服务政府和受监管行业；政府托管是利润率最高的板块。 - 2026年底IC3 Super West投运是增长拐点。 | https://www.macquariedatacentres.com | https://www.techpartner.news/news/macquarie-technology-group-sees-incremental-gains-in-fy26-eyes-modest-growth-in-fy27-628485 ¦ https://w.media/macquarie-data-centres-tops-out-47-mw-ic3-super-west/ ¦ https://dcnnmagazine.com/build/macquarie-tops-out-350m-47mw-ai-data-centre/ ¦ https://www.macquariedatacentres.com/data-centres/sydney/macquarie-park-campus/ic3-super-west/ | 2026-09-15
stack-infrastructure | STACK Infrastructure | STACK Infrastructure (APAC) | STACK Infrastructure | Colocation/Wholesale | United States | Denver (APAC HQ Singapore) | 2019 | Private (PE) | IPI Partners (now part of Blue Owl Capital); APAC portfolio in sale process (2026) with Macquarie, GIP/BlackRock AIP, Brookfield, IFM, KKR, DigitalBridge reported as interested |  | 36 | 290 | 4 | 1.3 | Hyperscale cloud providers (undisclosed); Hickory as Canberra/Perth development partner | STACK Infrastructure is a US hyperscale developer whose APAC portfolio, Australia included, is now up for sale. - Backed by IPI Partners (Blue Owl); entered Australia in 2022 via a partnership with builder Hickory. - MEL01 campus in Truganina (2 x 36MW) plus the adjacent 252MW MEL02 site with a dedicated 132kV substation. - ~300MW+ Australian platform across Melbourne, Canberra and Perth; a meaningful wholesale rival to AirTrunk and NEXTDC in Melbourne's west. - 2026 APAC sale process at a reported US$25bn+ valuation, drawing Macquarie, GIP, Brookfield and IFM interest. | STACK Infrastructure是美国超大规模开发商，含澳洲在内的亚太资产包正在出售。 - 由IPI Partners（Blue Owl）支持；2022年与建筑商Hickory合作进入澳洲。 - 墨尔本Truganina MEL01园区（2×36MW），毗邻252MW MEL02地块（自带132kV变电站）。 - 澳洲平台约300MW以上，覆盖墨尔本、堪培拉、珀斯；是墨尔本西区批发市场上AirTrunk与NEXTDC的重要对手。 - 2026年亚太资产包以逾250亿美元估值挂牌，Macquarie、GIP、Brookfield、IFM有意竞购。 | https://www.stackinfra.com/locations/asia-pacific/melbourne/mel02/ | https://www.stackinfra.com/locations/asia-pacific/melbourne/mel02/ ¦ https://constructionreviewonline.com/25bn-stack-apac-data-centers-draw-macquarie-bid-interest-as-ai-reshapes-construction-in-australia/ ¦ https://www.mingtiandi.com/real-estate/crelist/roundup-aip-brookfield-bid-for-stack-apac-data-centres/ ¦ https://www.globenewswire.com/news-release/2022/06/08/2459170/0/en/STACK-Infrastructure-Expands-APAC-Footprint-into-Australia-with-124MW-of-Capacity-across-Melbourne-Canberra-and-Perth.html ¦ https://www.datacentermap.com/australia/melbourne/stack-infrastructure-mel01a/ | 2026-09-15
digital-realty | Digital Realty | Digital Realty Australia | Digital Realty | Colocation/Wholesale | United States | Austin (AU HQ Sydney) | 2004 | Subsidiary of listed parent | Digital Realty Trust (NYSE: DLR). Note: SGX-listed Digital Core REIT holds no Australian assets; Australian sites sit on the parent balance sheet | NYSE:DLR | 50 |  | 5 |  | Hyperscale and enterprise tenants (undisclosed); anchor tenant at MEL10/11; IBM historically | Digital Realty is a global colocation major with a comparatively small and quiet Australian footprint. - Entered Australia in 2011; five facilities: SYD10 (6MW) and SYD11 (19MW) in Erskine Park, SYD13 (12MW planned), MEL10/MEL11 in Deer Park, Melbourne. - ~50MW of IT capacity per its 2020 disclosure, marketed within PlatformDIGITAL for enterprise and cloud interconnection. - Quiet during the AI build-out: the 2020 plan for 250MW in Western Sydney has not visibly progressed and adjacent land changed hands to ESR/Logos. | Digital Realty是全球托管巨头，但在澳洲布局较小、动作不多。 - 2011年进入澳洲，运营五座设施：Erskine Park的SYD10（6MW）、SYD11（19MW）及规划中SYD13（12MW），墨尔本Deer Park的MEL10/MEL11。 - 按2020年披露合计约50MW IT容量，纳入PlatformDIGITAL服务企业与云互联客户。 - 本轮AI扩建潮中相对低调：2020年宣布的西悉尼250MW计划未见实质进展，相邻地块已转手ESR/Logos。 | https://www.digitalrealty.com/data-centers/asia-pacific/sydney | https://www.datacenterdynamics.com/en/news/digital-realty-buys-two-20-acre-plots-western-sydney-250mw-plans/ ¦ https://www.datacenterdynamics.com/en/news/esr-acquires-land-in-sydney-previously-set-for-digital-realty-data-center/ ¦ https://www.digitalrealty.com/data-centers/asia-pacific/melbourne | 2026-09-15
aws | AWS | Amazon Web Services (Australia) | AWS | Hyperscaler (self-build) | United States | Seattle (AU HQ Sydney) | 2006 | Subsidiary of listed parent | Amazon.com Inc. (NASDAQ: AMZN) | NASDAQ:AMZN |  | 193.6 |  | 20 | Commonwealth Bank, NAB, Atlassian, Canva, Australian Government (Top Secret Cloud), Qantas, Telstra | AWS is the largest hyperscale tenant of Australian wholesale operators and a major self-builder. - Sydney region (ap-southeast-2) launched 2012, Melbourne region 2023; hosts the Australian Government's Top Secret Cloud. - Anchor tenant of AirTrunk, NEXTDC and CDC while also self-building. - June 2025: Amazon committed A$20bn over 2025-2029 to Australian data centre infrastructure, the largest technology investment in the country's history, paired with 170MW+ of new solar. - On 18 September 2026 NSW approved a A$2.17bn facility at 2 Glendenning Road, Glendenning in western Sydney: 235MW maximum electrical demand and 193.6MW IT load, lodged by Lehr Consultants International as proponent over Blacktown City Council objections. - Still does not disclose aggregate Australian MW or facility counts. | AWS是澳洲批发型运营商最大的超大规模租户，同时也在自建。 - 2012年开设悉尼区域（ap-southeast-2），2023年增设墨尔本区域；承载联邦政府绝密级云。 - 既是AirTrunk、NEXTDC、CDC的核心租户，也自建设施。 - 2025年6月亚马逊承诺2025-2029年投入200亿澳元建设澳洲数据中心，为该国史上最大科技投资，配套170MW以上新增光伏。 - 2026年9月18日，新州批准西悉尼Glendenning（2 Glendenning Road）项目，投资21.7亿澳元，最大用电需求235MW、IT负载193.6MW；申报主体为Lehr Consultants International，Blacktown City Council曾提出反对。 - 仍不披露澳洲在运MW总量及设施数量。 | https://aws.amazon.com/local/australia/ | https://www.aboutamazon.com/news/aws/amazon-data-center-investment-in-australia ¦ https://international.austrade.gov.au/en/news-and-analysis/success-stories/aws-plans-to-invest-a20-billion-to-expand-digital-infrastructure-in-australia-by-2029 ¦ https://www.datacenterdynamics.com/en/news/amazon-plans-to-invest-13bn-in-data-centers-in-australia-by-2029/ | 2026-10-07
microsoft | Microsoft | Microsoft Australia (Azure) | 微软 (Azure) | Hyperscaler (self-build) | United States | Redmond (AU HQ Sydney) | 1975 | Subsidiary of listed parent | Microsoft Corp. (NASDAQ: MSFT) | NASDAQ:MSFT |  | 190 | 29 | 25 | Australian Government (Azure Protected/Top Secret), Telstra, banks, OpenAI (Azure), enterprises | Microsoft is Australia's largest committed hyperscale investor, mixing self-build with leased wholesale halls. - Three Azure regions (Sydney, Melbourne, Canberra) across 29 sites. - Self-built campuses such as Kemps Creek alongside leased halls from AirTrunk, NEXTDC and CDC. - October 2023's A$5bn pledge was superseded in April 2026 by a A$25bn commitment to 2029, its largest ever Australian investment. - The 190MW Kemps Creek build is the flagship self-build in AEMO's connection pipeline. - On 1 October 2026 NSW approved a second western Sydney facility at Honeman Close, Huntingwood: 96MW IT load, A$1.26bn, assessed by the Department of Planning, Housing and Infrastructure. | 微软是在澳承诺投资规模最大的超大规模云商，自建与租赁并行。 - 运营悉尼、墨尔本、堪培拉三个Azure区域，共29个站点。 - 既有Kemps Creek等自建园区，也向AirTrunk、NEXTDC、CDC租赁批发机房。 - 2023年10月的50亿澳元承诺已于2026年4月升级为至2029年的250亿澳元，为其在澳最大投资。 - 190MW的Kemps Creek项目是AEMO并网管线中的旗舰自建工程。 - 2026年10月1日，新州规划部门批准西悉尼第二个站点Huntingwood的Honeman Close项目，IT负载96MW，投资12.6亿澳元。 | https://news.microsoft.com/source/asia/features/investing-in-australias-ai-future/ | https://news.microsoft.com/source/asia/features/investing-in-australias-ai-future/ ¦ https://www.cnbc.com/2026/04/23/microsoft-expands-ai-footprint-in-australia-with-18-billion-investment.html ¦ https://certifiedstrategic.com/insights/aemo-5-4gw-australian-data-centre-pipeline-june-2026 ¦ https://constructionreviewonline.com/microsoft-announces-plans-for-kemps-creek-project-in-australia/ | 2026-10-07
google | Google Cloud | Google Cloud Australia | 谷歌云 (Google Cloud) | Hyperscaler (self-build) | United States | Mountain View (AU HQ Sydney) | 1998 | Subsidiary of listed parent | Alphabet Inc. (NASDAQ: GOOGL) | NASDAQ:GOOGL |  |  |  | 1 | ANZ Bank, Woolworths, Optus, Australian Government agencies, Canva | Google Cloud is a major hyperscale tenant in Australia but, unlike Amazon and Microsoft, has made no large self-build commitment. - Sydney region (2017) and Melbourne region (2021), largely from leased wholesale capacity. - Committed A$1bn to its Digital Future Initiative in 2021. - A reported A$20bn AI/data centre hub was paused in March 2026 over concerns a local hub would trigger permanent-establishment tax treatment. - Assumed to be a key tenant behind several unnamed hyperscale contracts. | 谷歌云是澳洲重要的超大规模租户，但与亚马逊、微软不同，尚无大规模自建承诺。 - 运营悉尼（2017年）、墨尔本（2021年）两个区域，主要依托租赁批发容量。 - 2021年承诺10亿澳元'数字未来计划'。 - 据报200亿澳元AI/数据中心枢纽计划于2026年3月暂停，原因是担心触发'常设机构'税务认定。 - 市场普遍认为其是多笔未披露租户的超大规模合约背后的重要租户。 | https://cloud.google.com/about/locations | https://ia.acs.org.au/article/2026/google-pauses--20b-australian-data-centre-investment.html ¦ https://cloud.google.com/blog/products/infrastructure/the-google-cloud-region-in-melbourne-is-now-open/ ¦ https://www.datacenterdynamics.com/en/news/google-cloud-launches-new-region-in-melbourne-australia/ | 2026-09-15
oracle | Oracle | Oracle Cloud Infrastructure (Australia) | Oracle (OCI) | Hyperscaler (self-build) | United States | Austin (AU HQ Sydney) | 1977 | Subsidiary of listed parent | Oracle Corp. (NYSE: ORCL) | NYSE:ORCL |  |  |  |  | Australian Government (Oracle Government Cloud, Canberra), banks, universities, enterprises | Oracle is a demand-side hyperscaler exposure in Australia with no self-built campuses or disclosed MW. - OCI commercial regions in Sydney (2019) and Melbourne (2020), plus dedicated Australian Government Cloud regions launched in 2023. - All hosted in third-party colocation; a known NEXTDC and Equinix tenant. - Despite its global AI data centre push with OpenAI, told the market in March 2026 it has no Australian AI build plans, focusing on corporate and government cloud demand. | Oracle在澳洲属于需求端超大规模敞口，无自建园区，也未披露MW。 - OCI商业区域：悉尼（2019年）、墨尔本（2020年）；2023年推出专属澳洲政府云区域。 - 全部托管于第三方数据中心，是NEXTDC与Equinix的已知租户。 - 尽管在全球与OpenAI大举推进AI数据中心，2026年3月表示暂无在澳AI建设计划，重点仍是企业及政府云需求。 | https://www.oracle.com/anz/cloud/public-cloud-regions/ | https://www.capitalbrief.com/article/oracle-is-all-in-on-ai-data-centres-just-not-in-australia-c0862544-b284-44b0-84a5-e332840e9927/ ¦ https://www.datacenterdynamics.com/en/news/oracle-launches-government-cloud-region-in-australia/ ¦ https://www.oracle.com/anz/cloud/public-cloud-regions/ | 2026-09-15
firmus | Firmus Technologies | Firmus Technologies (Project Southgate) | Firmus (Project Southgate) | AI/GPU cloud | Australia | Sydney | 2019 | Private (PE) | Founders Oliver Curtis & Tim Rosenfeld; US$10bn debt facility led by Blackstone and Coatue (Feb 2026); US$505m equity round led by Coatue (Apr 2026); ~US$2bn of August 2026 commitments from Jane Street, Blackstone and NVIDIA; ASX IPO priced at A$11.00 per share for ~A$7.1bn (US$4.9bn) at an implied ~A$43.7bn, bookbuild 6-9 October 2026, debut targeted 22-23 October 2026 |  |  | 1600 |  | 73.3 | OpenAI (anchor for Malaysian capacity), Meta (reported: ~55,000 GPUs across Victorian and Tasmanian sites, plus Indonesian supply), AI labs and enterprises via NVIDIA DGX Cloud; the CDC Data Centres hosting relationship ended at 42MW | Firmus Technologies is Australia's largest AI/GPU cloud story and the vehicle taking NVIDIA, Blackstone and Coatue capital into local AI compute. - Sydney-headquartered, co-CEOs Oliver Curtis and Tim Rosenfeld; builds immersion-cooled 'AI factories' on NVIDIA's DSX design and sells GPU cloud rather than colocation. - Priced an ASX IPO at A$11.00 per share for ~A$7.1bn at an implied ~A$43.7bn - Australia's second-largest float; prospectus 8 October, debut targeted 22-23 October 2026. - Over 900MW contracted across seven sites globally with only two operating; Australian sites are Launceston and Bell Bay (288MW, lodged) in Tasmania, Melbourne and South Australia. - The 1.6GW, A$73.3bn Project Southgate partnership with CDC ended in October 2026 after only 42MW was deployed at CDC's Melbourne site; CDC cited Firmus' Asian expansion and funding scalability. - Tasmanian delivery is slowed by Hydro Tasmania supply priority and Marinus Link delays, shifting focus to the 600MW South Australian supply deal (c.2032 infrastructure). | Firmus是澳洲最大的AI/GPU云叙事，也是NVIDIA、Blackstone与Coatue资本进入本地AI算力的主要通道。 - 总部悉尼，联席CEO为Oliver Curtis与Tim Rosenfeld；基于NVIDIA DSX架构建设浸没式液冷"AI工厂"，出售GPU算力而非传统托管。 - ASX IPO定价每股11澳元，募资约71亿澳元，隐含估值约437亿澳元，为澳洲史上第二大IPO；10月8日递交招股书，拟10月22-23日挂牌。 - 全球七个站点签约容量逾900MW，目前仅两处在运；澳洲站点为塔州Launceston与Bell Bay（288MW，已申报）、墨尔本及南澳。 - 与CDC的1.6GW、733亿澳元Southgate合作已于2026年10月终止，实际仅在CDC墨尔本设施落地42MW；CDC方面称顾虑其亚洲扩张与资金可持续性。 - 塔州推进受制于Hydro Tasmania既有用户优先及Marinus Link延期，重心转向南澳600MW供电协议（配套设施约2032年到位）。 | https://firmus.co | https://firmus.co/newsroom/southgate-expansion ¦ https://firmus.co/newsroom/capital-raise-to-expand-project-southgate-nationally ¦ https://www.datacenterdynamics.com/en/news/firmus-secures-10bn-debt-financing-facility-for-project-southgate-ai-factory-roll-out/ ¦ https://dataxconnect.com/weekly-data-centre-news-3rd-july-2026/ | 2026-10-07
greensquaredc | GreenSquareDC | GreenSquareDC | GreenSquareDC | Colocation/Wholesale | Australia | Perth | 2022 | Private (PE) | Partners Group (Swiss PE), acquired March 2025 for ~A$1.2bn |  | 4 | 106 | 1 | 1.1 | Sharon AI (anchor of SYD1 stage 1, ~8,200 NVIDIA Blackwell Ultra GPUs from Q4 2026); enterprise, government and AI/GPU tenants (otherwise undisclosed) | GreenSquareDC is a Partners Group-owned hyperscale developer that illustrates both PE appetite for Australian DC and rising planning risk. - Founded in Perth in October 2022 by Walt Coulston as a sustainability-led developer. - Acquired by Swiss private-markets firm Partners Group in March 2025 for ~A$1.2bn. - Live asset: the former IBM data centre at 3 Brookhollow Avenue, Western Sydney (SYD1), expanding from 4MW to ~110MW. - September 2026: signed Sharon AI as long-term anchor for SYD1 stage 1, its first disclosed customer commitment, with ~8,200 NVIDIA Blackwell Ultra GPUs targeted from Q4 2026. - Flagship 120MW Perth WAi1 project at Hazelmere remains withdrawn after community and noise-assessment pushback in May 2026. | GreenSquareDC是Partners Group旗下的超大规模开发商，既体现PE对澳洲数据中心的热情，也暴露规划审批风险。 - 2022年10月由Walt Coulston在珀斯创立，定位可持续发展导向。 - 2025年3月被瑞士私募Partners Group以约12亿澳元收购。 - 现有资产为西悉尼3 Brookhollow Avenue原IBM数据中心（SYD1），从4MW扩至约110MW。 - 2026年9月与Sharon AI签订SYD1一期长期锚定合约，为其首个公开客户承诺，计划自2026年四季度部署约8,200张NVIDIA Blackwell Ultra GPU。 - 珀斯Hazelmere旗舰项目WAi1（120MW）在社区反对与噪声评估压力下于2026年5月撤回，至今未重启。 | https://greensquaredc.com | https://www.datacenterdynamics.com/en/news/australias-greensquaredc-expanding-data-center-in-greater-western-sydney/ ¦ https://bebeez.eu/2026/05/28/swiss-backed-greensquaredc-withdraws-application-for-120mw-data-center-in-perth-australia/ ¦ https://www.datacenterdynamics.com/en/news/partners-group-acquires-australian-data-center-firm-greensquaredc/ | 2026-10-07
dci-data-centers | DCI Data Centers | DCI Data Centers (Brookfield) | DCI Data Centers (Brookfield) | Colocation/Wholesale | Australia | Sydney | 2011 | Private (PE) | Brookfield Infrastructure (Brookfield Asset Management) and institutional partners, acquired 2018 | NYSE:BAM (parent) |  |  | 3 | 0.47 | Cloud and managed service providers, Defence and SA/federal government (Zone 3-5 security), enterprises | DCI Data Centers is Brookfield Infrastructure's Asia-Pacific data centre platform, headquartered in Sydney. - Operating sites at Eastern Creek (Sydney), Kidman Park (Adelaide, ADL01/02) and Auckland. - Developments at Canberra (CBR01, 25MW), Eastern Creek (SYD02/03), Mawson Lakes (ADL03) and Seoul. - Focus on secure, Zone 3-5 rated wholesale capacity for government and cloud/MSP customers. - Brookfield's reported interest in STACK's APAC assets in 2026 signals intent to scale DCI materially in Australia. | DCI Data Centers是Brookfield Infrastructure的亚太数据中心平台，总部悉尼。 - 在运站点：悉尼Eastern Creek、阿德莱德Kidman Park（ADL01/02）及奥克兰。 - 在建/规划：堪培拉CBR01（25MW）、Eastern Creek SYD02/03、Mawson Lakes ADL03及首尔。 - 主打面向政府和云/MSP客户的高安全等级（Zone 3-5）批发容量。 - 2026年Brookfield传出竞购STACK亚太资产，显示大幅扩张DCI澳洲业务的意图。 | https://dcidatacenters.com | https://dcidatacenters.com/locations/ ¦ https://dcidatacenters.com/about/ ¦ https://www.datacenterdynamics.com/en/news/dci-data-centers-submits-plan-for-25mw-data-center-in-canberra-australia/ ¦ https://channellife.com.au/story/dci-data-centers-to-build-400m-facility-in-sydney ¦ https://www.mingtiandi.com/real-estate/crelist/roundup-aip-brookfield-bid-for-stack-apac-data-centres/ ¦ https://www.brookfield.com/about-us/global-presence/australia | 2026-09-15
goodman | Goodman Group | Goodman Group | Goodman | Developer/Investor | Australia | Sydney | 1989 | ASX-listed | Widely held; CIC (China Investment Corp) historically a major holder; management led by Greg Goodman | ASX:GMG |  | 590 |  | 5.5 | Hyperscalers and AI companies (Microsoft, Anthropic reported as expected Project Atlas users); powered-shell and turnkey leases | Goodman Group is Australia's largest listed industrial property group (A$87bn AUM), now pivoting its development book to data centres. - Data centres represent 78% of A$19.7bn global work-in-progress; global power bank 6.4GW, of which 3.6GW secured. - Flagship: ~A$5-5.5bn, 500MW Project Atlas at Eastern Creek, under construction from September 2026 next to NEXTDC's S7. - Project Apollo at 4-10 Talavera Road, Macquarie Park (135MW, A$1.4bn) approved under NSW SSD in early September 2026. - Withdrew the 90MW Project Mars application at 12 Mars Road, Lane Cove on 28 September 2026, citing a policy and regulatory environment that had 'evolved significantly' since March 2025. - Remaining Sydney book includes a 90MW ABC studios redevelopment, 126MW at Guildford West and a 90MW former Eaton site at Mascot. | Goodman是澳洲最大的上市工业地产集团（管理资产870亿澳元），开发重心已转向数据中心。 - 数据中心占其全球197亿澳元在建项目的78%；全球电力储备6.4GW，其中已锁定3.6GW。 - 旗舰项目Eastern Creek的Project Atlas（约50-55亿澳元、500MW）于2026年9月开工，紧邻NEXTDC S7。 - Macquarie Park的Project Apollo（4-10 Talavera Road，135MW、14亿澳元）于2026年9月初获新州州重大项目批准。 - 2026年9月28日撤回Lane Cove 12 Mars Road的90MW申请，理由是政策与监管环境自2025年3月以来已大幅变化。 - 悉尼在手项目还包括原ABC电视台地块90MW、Guildford West 126MW及Mascot原Eaton仓库90MW。 | https://www.goodman.com | https://kalkine.com.au/news/announcements/goodman-group-reports-fy26-operating-profit-of-267-billion-data-centres-drive-wip-to-197-billion ¦ https://australiatimes.com/goodman-begins-construction-on-major-sydney-data-centre-as-ai-infrastructure-boom-accelerates ¦ https://www.forbes.com.au/news/innovation/nsw-pushes-goodman-to-back-fresh-power-for-5-5-billion-ai-factory/ ¦ https://www.datacenterdynamics.com/en/news/goodman-files-to-develop-90mw-data-center-campus-in-sydney-australia-2/ ¦ https://www.fool.com.au/2026/05/26/goodman-group-reports-87-1-billion-portfolio-value-as-data-centre-demand-grows/ | 2026-10-07
stockland | Stockland | Stockland (with EdgeConneX) | Stockland (EdgeConneX JV) | Developer/Investor | Australia | Sydney | 1952 | ASX-listed | Widely held; 50:50 data centre JV with EdgeConneX (EQT-owned) finalised March 2026 | ASX:SGP |  | 518 |  | 1.5 | Hyperscale tenants targeted via EdgeConneX (undisclosed) | Stockland, one of Australia's oldest diversified property groups, is monetising its industrial land bank through hyperscale data centres. - 50:50 JV with US operator EdgeConneX (EQT-owned) finalised in March 2026. - On 1 October 2026 NSW approved the A$630.4m Road 1 data centre at 1-5 Khartoum Road, Macquarie Park - a 10-storey building of 49MW (34.3MW IT load) adjoining a 76.4MW facility approved in March. - Other identified projects: a 168MW Western Sydney filing and a 250MW campus at Cherry Lane, Laverton North in Melbourne's west. - Management has flagged 5-10% of group capital (A$750m-1.5bn) for data centres, implying A$14-15bn of total project capital with partners. | Stockland是澳洲历史最悠久的综合地产集团之一，正以超大规模数据中心变现工业土地储备。 - 2026年3月与美国运营商EdgeConneX（EQT持有）成立50:50合资公司。 - 2026年10月1日，新州批准Macquarie Park的Road 1项目（1-5 Khartoum Road），10层楼、49MW（IT负载34.3MW）、6.304亿澳元，紧邻3月获批的76.4MW设施。 - 其余项目包括西悉尼168MW申报项目及墨尔本西部Laverton North的Cherry Lane 250MW园区。 - 管理层计划将集团5-10%资本（7.5-15亿澳元）投向数据中心，对应与合作方合计约140-150亿澳元项目资本。 | https://www.stockland.com.au | https://w.media/stockland-finalises-edgeconnex-data-centre-jv-as-ceo-plots-more-investment/ ¦ https://www.mingtiandi.com/real-estate/data-centres/stockland-seeks-approval-for-250mw-melbourne-data-centre-campus/ ¦ https://w.media/nsw-approves-stockland-data-centre-for-sydney-innovation-precinct/ ¦ https://inforcapital.com/news/stockland-files-to-build-168mw-data-center-in-sydney-australia/ | 2026-10-07
centuria-resetdata | Centuria / ResetData | Centuria Capital / Centuria Industrial REIT / ResetData | Centuria / ResetData | Developer/Investor | Australia | Sydney | 1998 | ASX-listed | Centuria Capital (ASX: CNI) manages Centuria Industrial REIT (ASX: CIP) and holds 50% of ResetData; A$300m equity raise June 2026 | ASX:CNI / ASX:CIP | 14.5 | 250 | 3 | 0.3 | Telstra (Melbourne 12MW), Fujitsu/Next Capital (Perth Malaga), ResetData sovereign AI cloud tenants; CDC (7-10MW hosting MSA) | Centuria Capital is the clearest 'sheds-to-digital' pivot among ASX REITs, via Centuria Industrial REIT and a 50% stake in ResetData. - Centuria Industrial REIT owns three small operating data centres: a 12MW Telstra-leased site in Melbourne, a Fujitsu-occupied facility in Malaga, Perth, and the 2.5MW Wellcamp centre in Toowoomba. - Converting industrial land at Yarraville, Thomastown and Hazelmere into a 250MW+ pipeline, supported by 72MW of dedicated on-site generation and a A$165m Macquarie bridge facility. - ResetData is an immersion-cooled sovereign AI cloud provider deploying NVIDIA GPUs in Melbourne and inside CDC facilities under a 7-10MW hosting MSA. - On 29 September 2026 Monash Council rejected the 38MW, A$137m expansion of the Telstra-occupied Clayton site against officer recommendation, citing power demand, cooling noise and the new Victorian separation test; the building sits ~80m from housing. - A second 40MW application on the same site remains pending under Victoria's Sustainable Data Centre Action Plan, which proposes a 150m residential buffer and own-renewables supply. | Centuria Capital是ASX REIT中从物流仓储转向数字基础设施最鲜明的案例，载体为Centuria Industrial REIT与ResetData 50%股权。 - Centuria Industrial REIT持有三座小型在运数据中心：墨尔本12MW Telstra租赁站点、珀斯Malaga的Fujitsu使用设施、Toowoomba 2.5MW Wellcamp。 - 将Yarraville、Thomastown、Hazelmere工业用地转化为250MW以上管线，配套72MW自建电源及Macquarie 1.65亿澳元过桥融资。 - ResetData为浸没式液冷主权AI云服务商，在墨尔本及CDC设施内（7-10MW托管主协议）部署NVIDIA GPU。 - 2026年9月29日，Monash Council否决Clayton站点38MW、1.37亿澳元扩建申请，推翻规划官员的批准建议，理由是用电需求、冷却噪声及维州新设的间距要求；建筑距住宅仅约80米。 - 同一地块另一宗40MW申请仍在审，适用维州Sustainable Data Centre Action Plan，该方案拟要求距住宅150米并自备可再生电源。 | https://centuria.com.au/our-capabilities/data-centres/ | https://www.datacenterdynamics.com/en/news/centuria-eyes-250mw-of-data-center-capacity-in-australia/ ¦ https://www.theindustrialist.com.au/news/2026/08/13/centuria-and-resetdata-accelerate-250mw-ai-and-digital-pipeline/1786586491 ¦ https://realassets.ipe.com/news/centuria-capital-raises-a300m-for-resetdata-data-centre-expansion/10137378.article ¦ https://www.fool.com.au/2026/06/16/centuria-industrial-reit-unveils-data-centre-strategy/ | 2026-10-07
ispt | ISPT | ISPT (IFM Investors) | ISPT (IFM Investors) | Developer/Investor | Australia | Melbourne | 1994 | Private | Owned by Australian industry superannuation funds; merged with IFM Investors (2025) | [5 empty] | n/a (landowner/developer) - sold Kemps Creek campus site to AirTrunk | ISPT is a super-fund-owned unlisted property investor, now part of IFM Investors, pursuing land-and-power arbitrage rather than operating data centres. - Used its Western Sydney industrial land at Mamre Road, Kemps Creek to secure planning for a six-building, up-to-1GW data centre campus. - Agreed in November 2025 to sell the site to AirTrunk. - Exemplifies Australian institutional landowners monetising powered land rather than operating. - IFM Investors separately appears as a bidder for STACK's APAC portfolio. | ISPT是行业养老金持有的非上市地产投资机构（现并入IFM Investors），走'土地+电力'套利路线而非自营数据中心。 - 利用西悉尼Kemps Creek Mamre Road工业用地取得六栋楼、最高1GW数据中心园区规划许可。 - 2025年11月同意将地块出售给AirTrunk。 - 代表澳洲机构地主变现带电土地、不做运营的模式。 - IFM Investors另被报道为STACK亚太资产竞购方之一。 | https://www.ispt.net.au | https://bebeez.eu/2025/11/11/airtrunk-set-to-buy-planned-1gw-data-center-site-in-western-sydney-australia/ ¦ https://www.datacentermap.com/australia/sydney/mamre-road-data-centre-campus/ ¦ https://www.datacenterdynamics.com/en/news/plans-filed-for-1gw-data-center-campus-in-sydney-australia/ | 2026-09-15
telstra-infraco | Telstra InfraCo | Telstra InfraCo Data Centres | Telstra InfraCo | Telco/Carrier | Australia | Melbourne | 2020 | Subsidiary of listed parent | Telstra Group (ASX: TLS); Minchinbury project with Starwood Capital and Doma Infrastructure Group | ASX:TLS |  | 62 | 3 |  | Telstra, Australian Government (HCF Strategic certified), carriers and enterprises | Telstra InfraCo is the infrastructure arm of Telstra, Australia's incumbent telco, taking a capital-light 'connectivity-first' approach to data centres. - Holds 250,000km of fibre plus three carrier-neutral data centres in Sydney (St Leonards), Melbourne (Clayton) and Canberra (Deakin), ~44.5MW target IT capacity. - Does not compete in hyperscale; contributes land and fibre to the 62MW Minchinbury AI campus financed and operated by Starwood Capital and Doma. - Gives Telstra shareholders indirect exposure to the data centre cycle via fibre demand and ground leases. | Telstra InfraCo是澳洲电讯Telstra的基础设施部门，以轻资本的'连接优先'路线参与数据中心。 - 拥有25万公里光纤及三座运营商中立数据中心（悉尼St Leonards、墨尔本Clayton、堪培拉Deakin），目标IT容量约44.5MW。 - 不直接参与超大规模竞争；以土地和光纤入股由Starwood Capital与Doma出资运营的62MW Minchinbury AI园区。 - 为Telstra股东提供通过光纤需求与土地租赁间接参与数据中心周期的敞口。 | https://www.telstrawholesale.com.au/wholesaleconnect/category/technology/key-benefits-of-telstra-infraco-data-centres.html | https://certifiedstrategic.com/insights/telstra-s-data-centre-disconnect-headcount-out-hyperscale-in ¦ https://www.prnewswire.com/apac/news-releases/starwood-capital-group-doma-infrastructure-group-and-telstra-infraco-announce-agreement-to-develop-62mw-ai-optimised-data-centre-in-western-sydney-302613655.html ¦ https://www.datacenterdynamics.com/en/news/starwood-doma-and-telstra-plan-62mw-data-center-in-sydney/ | 2026-09-15
vocus | Vocus | Vocus | Vocus | Telco/Carrier | Australia | Melbourne | 2008 | Private (PE) | Macquarie Asset Management (MAM) and Aware Super consortium, took private 2021 (A$3.5bn) |  |  |  |  | 5.25 | Government, wholesale carriers, hyperscalers (dark fibre to data centres), enterprises; connects to 150 data centres | Vocus is Australia's largest independent fibre and network operator - a picks-and-shovels play on data centre traffic rather than a capacity owner. - Owned by Macquarie Asset Management and Aware Super since its 2021 take-private. - 50,000km+ of owned fibre, ~15,000km of subsea cable and a handful of small legacy colocation sites; connects to about 150 data centres. - The A$5.25bn acquisition of TPG's enterprise, government and wholesale fixed assets (completed August 2025) makes it the key backbone linking the Sydney/Melbourne hyperscale clusters, regional Australia and international cables. - On 25 September 2026 it announced a 4,000km ducted Brisbane-Darwin route via Townsville under its Australian Digital Infrastructure Platform: up to 3,456 fibre strands, service from 2030, aimed at emerging QLD and NT data centre precincts. - Second ADIP project after quadrupling capacity on the Adelaide-Perth 2 route. | Vocus是澳洲最大的独立光纤与网络运营商，属于数据中心流量增长的"铲子型"受益者，而非容量持有者。 - 2021年私有化后由Macquarie Asset Management与Aware Super持有。 - 自有光纤5万公里以上、海缆约1.5万公里，另有少量小型传统托管站点，接入约150座数据中心。 - 2025年8月完成对TPG企业、政府及批发固网资产的52.5亿澳元收购，成为连接悉尼/墨尔本超大规模集群、区域澳洲与国际海缆的关键骨干。 - 2026年9月25日宣布在Australian Digital Infrastructure Platform下新建布里斯班经Townsville至达尔文的4,000公里管道光缆，最多3,456芯，2030年投入服务，面向昆州与北领地新兴数据中心集群。 - 这是继Adelaide-Perth 2线路扩容四倍后ADIP的第二个项目。 | https://www.vocus.com.au | https://www.datacenterdynamics.com/en/news/vocus-closes-acquisition-of-tpg-telecoms-fiber-assets/ ¦ https://www.vocus.com.au/about-vocus/our-network/australia ¦ https://www.accc.gov.au/media-release/vocus%E2%80%99-proposed-acquisition-of-tpg-enterprise-government-and-wholesale-business-not-opposed | 2026-10-07
fujitsu-au-dc-next-capital | Fujitsu DCs (Next Capital) | Fujitsu Australia Data Centres (sold to Next Capital) | Fujitsu 澳洲数据中心 (Next Capital) | Colocation/Wholesale | Australia | Sydney |  | Private (PE) | Next Capital Fund V (Australian PE), acquisition agreed July 2026 for just under A$200m (AFR); previously Fujitsu Ltd (TYO: 6702) |  | 25 | 75 | 5 | 0.2 | ~130 enterprise and government clients (~7MW leased); Fujitsu managed services | Fujitsu's Australian data centres are being carved out to Next Capital as an independent, Australian-managed enterprise colocation platform. - Fujitsu built one of Australia's larger enterprise colocation footprints in the 2000s-2010s: the Western Sydney (Greystanes) campus plus Homebush, Noble Park, Eight Mile Plains and Malaga. - July 2026: agreed to sell the five-site business - 25MW operational, ~7MW leased to ~130 clients, ~100MW expansion potential - to mid-market PE firm Next Capital for just under A$200m; North Ryde retained. - The carve-out brings brownfield expansion optionality under new ownership. | Fujitsu澳洲数据中心正分拆出售给Next Capital，将成为澳洲团队管理的独立企业级托管平台。 - Fujitsu在2000至2010年代建立了澳洲规模较大的企业托管布局：西悉尼Greystanes园区及Homebush、Noble Park、Eight Mile Plains、Malaga站点。 - 2026年7月同意以略低于2亿澳元出售五站业务（在运25MW，约7MW出租给约130家客户，可扩至约100MW）给中型PE Next Capital；North Ryde保留。 - 分拆后具备存量扩建的期权价值。 | https://www.fujitsu.com/au/ | https://www.datacenterdynamics.com/en/news/fujitsu-sells-australian-data-center-business-to-next-capital/ ¦ https://www.itnews.com.au/news/fujitsu-sells-five-australian-data-centres-627511 ¦ https://www.cyberdaily.au/digital-transformation/13935-private-equity-firm-buys-5-australian-data-centres-from-fujitsu | 2026-09-15
interactive | Interactive | Interactive | Interactive | Colocation/Wholesale | Australia | Melbourne | 1988 | Private | Privately owned (founder family/management); describes itself as Australia's largest privately owned IT services provider |  |  |  | 3 |  | 380+ enterprise and government customers; banks, retailers, universities | Interactive is a niche, enterprise-focused colocation operator rather than a hyperscale player. - Melbourne-based, privately owned IT services company founded in 1988. - Three carrier-neutral colocation data centres in Port Melbourne, St Leonards (Sydney) and Eight Mile Plains (Brisbane), plus hardware maintenance, cloud and cyber services. - Serves mid-market enterprise and government customers with rack densities from 2kW to 100kW; does not disclose MW capacity. | Interactive是聚焦企业市场的细分托管运营商，不参与超大规模竞争。 - 1988年成立、总部墨尔本的私营IT服务公司。 - 在Port Melbourne、悉尼St Leonards、布里斯班Eight Mile Plains运营三座运营商中立托管数据中心，兼营硬件维护、云及网络安全服务。 - 服务中型企业与政府客户，机柜密度2kW至100kW；未披露MW容量。 | https://www.interactive.com.au/services/data-centres/ | https://www.interactive.com.au/services/data-centres/locations/ ¦ https://www.datacentermap.com/c/interactive-pty-ltd/ | 2026-09-15
leading-edge-dc | Leading Edge DC | Leading Edge Data Centres | Leading Edge DC | Colocation/Wholesale | Australia | Newcastle | 2019 | Private | Founder/CEO Chris Thorpe; Washington H. Soul Pattinson (ASX: SOL) backed A$20m raise (2020) |  |  |  | 6 | 0.02 | Regional councils (City of Newcastle), MSPs, regional enterprises, carriers | Leading Edge Data Centres is a small but relevant 'regional edge' player as hyperscale build-out concentrates in Sydney and Melbourne. - Founded in 2019 by Chris Thorpe; backed by Washington H. Soul Pattinson. - Builds Tier III-designed edge data centres in regional NSW using Schneider Electric prefabricated modules. - Six sites (Newcastle, Tamworth, Dubbo, Albury, Coffs Harbour, Wagga Wagga), each sub-2MW. - Targets regional councils, MSPs and businesses needing low-latency local hosting. | Leading Edge Data Centres是'区域边缘'细分市场中规模虽小但有代表性的参与者，与集中于悉尼、墨尔本的超大规模建设形成对照。 - 2019年由Chris Thorpe创立，获Washington H. Soul Pattinson支持。 - 采用Schneider Electric预制模块，在新州区域城镇建设Tier III级边缘数据中心。 - 六座站点（Newcastle、Tamworth、Dubbo、Albury、Coffs Harbour、Wagga Wagga），单站2MW以下。 - 服务需要本地低时延托管的区域政府、MSP和企业。 | https://leadingedgedc.com | https://leadingedgedc.com/ ¦ https://www.datacenterdynamics.com/en/news/leading-edge-dc-pumps-13m-nsw-data-center-campus/ ¦ https://www.datacentermap.com/c/leading-edge-dc/ | 2026-09-15
edge-centres | Edge Centres | Edge Centres | Edge Centres | Colocation/Wholesale | Australia | Brisbane | 2020 | Private | Founder/CEO Jonathan Eaves and private investors |  |  |  | 8 |  | Regional ISPs, MSPs, content/CDN providers, telcos (tower co-location with Everest Infrastructure) | Edge Centres is an off-grid/renewable edge niche player, immaterial to national MW totals. - Founded in 2020 by Jonathan Eaves; deploys small solar-powered, battery-backed edge data centres (64 quarter-racks per site) in regional towns; since expanded into the United States. - ~Eight Australian sites across Queensland, NSW, Victoria and Tasmania. - Targets ISPs, CDNs and enterprises wanting compute close to regional users; capacity per site well under 1MW. | Edge Centres是离网/可再生边缘细分领域的代表，对全国MW总量影响可忽略。 - 2020年由Jonathan Eaves创立，在区域城镇部署光伏供电、电池备份的小型边缘数据中心（每站64个四分之一机柜）；已拓展至美国。 - 澳洲约八个站点，覆盖昆州、新州、维州、塔州。 - 面向希望算力贴近区域用户的ISP、CDN和企业；单站容量远低于1MW。 | https://edgecentres.com | https://www.datacenterdynamics.com/en/news/edge-centres-files-permission-for-facility-in-bendigo-australia/ ¦ https://edgecentres.com/about-us/ | 2026-09-15
polaris | Polaris | Polaris Data Centre | Polaris Data Centre | Colocation/Wholesale | Australia | Springfield (Brisbane) | 2009 | Private | Springfield City Group (Maha Sinnathamby's Greater Springfield developer); Suncorp sold down its stake in 2012; managed by Veolia |  |  |  | 1 |  | Queensland Government agencies, corporates, MSPs; hub of Springfield dark-fibre network | Polaris Data Centre is a single-site regional Tier III operator in Brisbane's south-west with no announced AI-era expansion. - Opened in 2009 in Springfield Central as one of Australia's first purpose-built Tier III facilities; developed by Springfield City Group (Suncorp an early co-owner). - Anchors Greater Springfield's 720-core dark-fibre network. - Serves Queensland Government and corporate tenants under Veolia facility management. | Polaris Data Centre是布里斯班西南的单站点区域Tier III运营商，尚无AI时代扩建计划。 - 2009年在Springfield Central开业，为澳洲最早的专建Tier III设施之一；由Springfield City Group开发（Suncorp曾为早期共同持有人）。 - 是大Springfield地区720芯暗光纤网络的核心节点。 - 在Veolia设施管理下服务昆州政府及企业租户。 | https://www.polarisdatacentre.com.au | https://www.polarisdatacentre.com.au/about-us/ ¦ https://www.itnews.com.au/news/suncorp-sells-down-polaris-data-centre-share-291793 | 2026-09-15
blackstone | Blackstone | Blackstone (Australian DC exposure) | Blackstone | Developer/Investor | United States | New York | 1985 | Private (PE) | NYSE-listed alternative asset manager (NYSE: BX); Australian DC exposure via AirTrunk (with CPP Investments) and Firmus debt | NYSE:BX |  |  |  | 24 | n/a (investor) | Blackstone is the world's largest alternative asset manager and the largest single foreign investor in Australian data centres. - Acquired AirTrunk for A$24bn in September 2024 with CPP Investments; describes it as the cornerstone of a US$70bn+ global data centre portfolio (QTS, AirTrunk, Lumina). - Co-led the US$10bn Firmus debt facility with Coatue in February 2026 and was among the ~US$2bn of August 2026 Firmus cornerstone commitments alongside Jane Street and NVIDIA. - The ~US$1.5bn Singapore REIT to recycle AirTrunk's stabilised assets had still not launched as at 7 October 2026, despite a September-October target. - Its build-then-spin behaviour, plus the concurrent STACK APAC sale process, is the key read on Australian DC exit pricing. - Firmus' October 2026 IPO at ~A$43.7bn is the first visible mark on Blackstone's Australian AI-compute credit exposure. | Blackstone是全球最大另类资产管理公司，也是澳洲数据中心最大的单一外资投资者。 - 2024年9月与CPP Investments以240亿澳元收购AirTrunk，视其为逾700亿美元全球数据中心组合（QTS、AirTrunk、Lumina）的基石。 - 2026年2月与Coatue联合牵头100亿美元Firmus债务融资；2026年8月又与Jane Street、NVIDIA一道参与约20亿美元Firmus基石认购。 - 原定9-10月发行、约15亿美元的AirTrunk成熟资产新加坡REIT，至2026年10月7日仍未启动。 - 其"建成即分拆"的操作，加上同期STACK亚太资产出售流程，是判断澳洲数据中心退出定价的主要线索。 - Firmus 2026年10月以约437亿澳元估值上市，为Blackstone在澳AI算力信贷敞口提供了首个可见定价。 | https://www.blackstone.com | https://www.blackstone.com/news/press/blackstone-announces-agreement-to-acquire-airtrunk-in-a-a24b-transaction/ ¦ https://www.realestatesource.com.au/blackstone-weighs-airtrunk-asset-spin-off/ ¦ https://www.datacenterdynamics.com/en/news/firmus-secures-10bn-debt-financing-facility-for-project-southgate-ai-factory-roll-out/ | 2026-10-07
zerra-dc | Zerra DC | Zerra DC (data centre platform of AGP Sustainable Real Assets) | Zerra DC | Colocation/Wholesale | Singapore | Singapore |  | Private (PE) | Data centre arm of Singapore-based AGP Sustainable Real Assets; Western Downs development consortium with Macquarie Capital and Australian Data Centres (majority owned by Dexus) |  |  | 1440 | 1 | 31.9 | Anthropic (anchor tenant of stage 1, Claude inference workloads; subject to FIRB approval) | Zerra DC is the Singapore developer behind Australia's largest proposed data centre campus, anchored by Anthropic. - Data centre arm of AGP Sustainable Real Assets, developing Western Downs Digital Park on a 725ha site at Kogan near Dalby, QLD, about 250km west of Brisbane. - Development application lodged with Western Downs Regional Council in August 2026: A$31.9bn headline, of which A$14.5bn for the initial development. - Designed for 1.44GW of planned capacity, extendable to 2.16GW of peak capacity across six buildings, using closed-loop air cooling to limit water use. - In September 2026 Anthropic signed Australia's first AI-lab data centre lease, taking stage 1 for Claude inference rather than model training; still subject to FIRB and council approval. - Queensland accepted a mixed energy supply including coal and gas with no new transmission required; first capacity targeted 2027, full build-out 4-6 years, ~1,000 ongoing jobs. | Zerra DC是澳洲在建规模最大拟建园区的新加坡开发商，由Anthropic作为锁定租户。 - 系AGP Sustainable Real Assets旗下数据中心平台，在昆州Dalby附近Kogan的725公顷地块开发Western Downs Digital Park，距布里斯班约250公里。 - 2026年8月向Western Downs Regional Council递交开发申请，总投资口径319亿澳元，其中首期145亿澳元。 - 规划容量1.44GW，六栋建筑满建峰值可达2.16GW，采用闭式风冷以压低水耗。 - 2026年9月Anthropic签下澳洲首宗AI实验室数据中心租约，承租一期，用于Claude推理而非模型训练；仍需FIRB与地方议会批准。 - 昆州接受含煤电、燃气的混合供电且无需新建输电网；首批容量目标2027年，满建需4-6年，长期岗位约1,000个。 |  | https://www.abc.net.au/news/2026-09-16/queensland-data-centre-anthropic-dalby/107160640 ¦ https://www.mingtiandi.com/real-estate/data-centres/anthropic-to-lease-phase-1-of-zerra-dc-queensland-data-centre/ ¦ https://convergedigest.com/anthropic-zerra-dc-australia-2-16gw-data-center/ ¦ https://www.abc.net.au/news/2026-09-14/western-downs-digital-park-data-centre-energy-queensland/107115082 ¦ https://www.itnews.com.au/news/anthropic-signs-first-australian-data-centre-agreement-628972 | 2026-10-07
hyperdc | HyperDC | HyperDC Pty Ltd | HyperDC | Developer/Investor | Australia | Melbourne |  | Private | Privately held; director Gerard Adamsons, previously of residential developer Villawood Properties; financial backers not disclosed |  |  | 400 | 1 |  |  | HyperDC is a new Victorian developer that filed for a 400MW campus west of Melbourne in September 2026. - Private Melbourne company; its named director came out of residential developer Villawood Properties, and its funding is not disclosed. - Planning permit application lodged with the Victorian government on 29 September 2026 for 715 Ballan Road, Moorabool - 39ha of largely vacant land about 75km west of Melbourne. - 400MW of proposed IT load would make it one of the largest single campuses outside Sydney and a material addition to the Victorian pipeline. - The site sits next to AusNet's Moorabool Terminal Station and the 300MW Victorian Big Battery, an unusually direct transmission and firming position. - Filed as Victoria's Sustainable Data Centre Action Plan took effect, so own-renewables supply and the proposed 150m residential buffer are the key approval tests. | HyperDC是维州新面孔，2026年9月为墨尔本以西一处400MW园区递交规划申请。 - 墨尔本本地私人公司，具名董事出身住宅开发商Villawood Properties，资金来源未披露。 - 2026年9月29日就Moorabool的715 Ballan Road向维州政府申报规划许可，地块39公顷、基本空置，距墨尔本约75公里。 - 拟建IT负载400MW，将成为悉尼以外单体最大园区之一，对维州管线是实质性增量。 - 地块紧邻AusNet的Moorabool Terminal Station及300MW Victorian Big Battery，并网与调峰条件罕见地直接。 - 申报时点正值维州Sustainable Data Centre Action Plan落地，自备可再生电源与拟议的150米住宅间距将是审批关键。 |  | https://www.datacenterdynamics.com/en/news/plans-filed-for-400mw-data-center-campus-outside-melbourne-australia/ ¦ https://dataxconnect.com/weekly-data-centre-news-2nd-october-2026 | 2026-10-07
sharon-ai | Sharon AI | Sharon AI, Inc. | Sharon AI | AI/GPU cloud | United States | New York |  | NASDAQ-listed | Nasdaq-listed following a US$125m IPO in February 2026; US$100m convertible note (Dec 2025) and a USD.AI debt facility of up to US$500m | SHAZ |  |  | 1 |  | Canva; ESDS Software Solutions (US$1.25bn cloud capacity agreement); an unnamed global technology company (~US$950m); AI-native, research, government and hyperscale cohorts | Sharon AI is an Australian-founded GPU cloud (neocloud) that listed on Nasdaq in February 2026 and buys, rather than builds, most of its Australian capacity. - Nasdaq: SHAZ, headquartered in New York but positioned as an Australian neocloud; group capacity of 212MW is reported as online or in development. - Takes colocation from Equinix Sydney, NEXTDC Melbourne and CDC and, from September 2026, the first stage of GreenSquareDC's SYD1 in Western Sydney. - At SYD1 it will deploy about 8,200 NVIDIA Blackwell Ultra GPUs from Q4 2026, part of roughly 64,000 GPUs targeted by mid-2027. - Bought the former Visy / Norske Skog paper mill at Ettamogah near Albury, NSW for about A$50m in September 2026 - its first owned Australian site, with Visy staying on as a warehouse tenant. - Contracted revenue includes a US$1.25bn agreement with ESDS Software Solutions and a c.US$950m contract with an unnamed global technology company. | Sharon AI是起家于澳洲的GPU云（neocloud），2026年2月在Nasdaq上市，澳洲容量以租赁为主、自建为辅。 - Nasdaq代码SHAZ，总部纽约，但自我定位为澳洲neocloud；公开口径集团在运及在建容量212MW。 - 向Equinix悉尼、NEXTDC墨尔本及CDC租赁机柜，2026年9月起再承租GreenSquareDC西悉尼SYD1一期。 - SYD1计划自2026年四季度部署约8,200张NVIDIA Blackwell Ultra GPU，属其2027年年中前约64,000张GPU目标的一部分。 - 2026年9月以约5,000万澳元买下新州Albury附近Ettamogah的原Visy／Norske Skog纸厂，为其澳洲首个自有地块，Visy继续作为仓储租户留用。 - 已签约收入包括与ESDS Software Solutions的12.5亿美元算力协议，以及与一家未具名全球科技公司约9.5亿美元的合约。 |  | https://www.datacenterdynamics.com/en/news/sharonai-buys-former-printing-press-outside-albury-australia/ ¦ https://www.datacenterdynamics.com/en/news/sharon-ai-to-lease-capacity-from-australias-greensquaredc/ ¦ https://www.sec.gov/Archives/edgar/data/2068385/000149315226014405/ex99-1.htm ¦ https://www.abc.net.au/news/2026-09-16/visy-paper-mill-ettamogah-sharon-ai-computing/107150434 ¦ https://www.datacenterdynamics.com/en/news/sharon-ai-signs-125bn-cloud-capacity-agreement-with-esds-software-solutions/ | 2026-10-07
iren | IREN | IREN Limited | IREN | AI/GPU cloud | United States | New York | 2018 | NASDAQ-listed | Widely held Nasdaq-listed company; founded and led by Daniel and Will Roberts; Australian-incorporated with US head office | IREN |  | 800 | 1 |  | Not announced for the Australian campus; group AI cloud contracts are with US hyperscale and AI customers | IREN is a Nasdaq-listed, Australian-founded AI cloud and data centre owner returning to Australia with an 800MW campus. - Started as bitcoin miner Iris Energy in 2018 and is now a vertically integrated AI cloud operator running large GPU fleets. - Announced its first Australian data centre campus in June 2026 at Bundey, South Australia, about 125km northeast of Adelaide. - Four 330kV feeder exits are secured at the utility substation, supporting up to 800MW without network augmentation - a rare pre-cleared grid position. - Energisation is expected to begin in 2028, into a South Australian grid targeting 100% net renewables from 2027. - Subsea fibre is planned to link the campus to Singapore, Indonesia, South Korea and Japan; over 200 permanent and 500+ construction roles projected. | IREN是在Nasdaq上市、起家于澳洲的AI云与数据中心持有方，以800MW园区重返澳洲市场。 - 前身为2018年成立的比特币矿企Iris Energy，现已转型为垂直整合的AI云运营商，自营大规模GPU集群。 - 2026年6月公布澳洲首个数据中心园区，位于南澳Bundey，距阿德莱德东北约125公里。 - 已在公用变电站锁定四路330kV出线，无需电网增容即可支撑最高800MW，这种预先落实的并网条件在澳洲少见。 - 预计2028年开始并网送电，届时南澳电网目标为2027年起实现净100%可再生。 - 规划海缆连接新加坡、印尼、韩国、日本；预计长期岗位逾200个、施工期岗位500个以上。 | https://iren.com | https://iren.gcs-web.com/static-files/89f56bc3-0473-4a1b-a863-c6a3dba11018 ¦ https://itbrief.com.au/story/iren-signs-deal-for-800mw-south-australia-data-centre ¦ https://www.capitalbrief.com/briefing/iren-announces-south-australia-data-centre-campus-cc4cb085-d612-45e7-aee6-ed12b7c7e6b8/ | 2026-10-07

## OperatorMoves
operator_id | date | headline_en | headline_zh | source
airtrunk | 2025-11 | AirTrunk agrees to buy ISPT's Mamre Road, Kemps Creek site planned for up to 1GW (A$5bn project) | 拟购ISPT Kemps Creek Mamre Road地块，规划最高1GW、50亿澳元 | https://bebeez.eu/2025/11/11/airtrunk-set-to-buy-planned-1gw-data-center-site-in-western-sydney-australia/
airtrunk | 2025-12 | AirTrunk acquires north-west Melbourne site for 354MW MEL2 campus; A$5bn investment, Melbourne platform >630MW | 购入墨尔本西北地块建354MW MEL2，投资50亿澳元，墨尔本合计超630MW | https://airtrunk.com/airtrunk-expands-australian-platform-with-a-second-hyperscale-data-centre-campus-in-melbourne/
airtrunk | 2026-04 | Kemps Creek 1.2GW campus (A$5bn+) under NSW assessment; EPA seeks more information amid community objections | Kemps Creek 1.2GW园区（50亿澳元+）新州审批中，EPA要求补充资料 | https://ia.acs.org.au/article/2026/concern-over-australia-s-most-power-hungry-data-centre.html
airtrunk | 2026-07 | Blackstone/CPP prepare Singapore-listed REIT of mature AirTrunk assets incl. MEL1 (185MW+); ~US$1.5bn raise, up to US$4.4bn portfolio value | Blackstone/CPP筹备AirTrunk成熟资产新加坡REIT，募资约15亿美元 | https://www.realestatesource.com.au/blackstone-weighs-airtrunk-asset-spin-off/
aws | 2025-06 | Amazon commits A$20bn (2025-2029) to expand Sydney and Melbourne data centre infrastructure - largest tech investment in Australian history; three new solar farms (170MW+) | 亚马逊承诺2025-29年投200亿澳元扩建悉尼、墨尔本DC，配三座光伏（170MW+） | https://www.aboutamazon.com/news/aws/amazon-data-center-investment-in-australia
aws | 2025-06 | Austrade: AWS investment to underpin AI and cloud capacity, with 11 renewable projects generating ~1.4TWh p.a. | Austrade：AWS投资支撑AI与云容量，11个可再生项目年发电约1.4TWh | https://international.austrade.gov.au/en/news-and-analysis/success-stories/aws-plans-to-invest-a20-billion-to-expand-digital-infrastructure-in-australia-by-2029
blackstone | 2024-09 | Agrees to acquire AirTrunk for A$24bn implied EV with CPP Investments - largest APAC data centre deal | 与CPP Investments以240亿澳元EV收购AirTrunk，亚太最大数据中心交易 | https://www.blackstone.com/news/press/blackstone-announces-agreement-to-acquire-airtrunk-in-a-a24b-transaction/
blackstone | 2026-02 | Co-leads US$10bn debt facility for Firmus' Project Southgate with Coatue | 与Coatue共同牵头为Firmus Southgate项目提供100亿美元债务融资 | https://www.datacenterdynamics.com/en/news/firmus-secures-10bn-debt-financing-facility-for-project-southgate-ai-factory-roll-out/
blackstone | 2026-07 | Preparing Singapore REIT spin-off of stabilised AirTrunk assets (incl. MEL1) to recycle capital | 筹备将AirTrunk成熟资产（含MEL1）分拆为新加坡REIT以回收资本 | https://www.realestatesource.com.au/blackstone-weighs-airtrunk-asset-spin-off/
cdc | 2025-02 | Future Fund lifts stake to 34.5% and Infratil to 49.7% as CSC sells 12% | Future Fund增持CDC至34.5%、Infratil至49.7%；CSC出售12% | https://www.futurefund.gov.au/news-room/Future-Fund-acquires-further-shares-in-CDC
cdc | 2026-04 | Moody's assigns Baa2 (stable) rating; A$1bn hybrid issued and A$500m shareholder equity injection (Feb) to fund build-out | 穆迪授予CDC Baa2（稳定）评级；发行10亿澳元混合资本、股东注资5亿澳元 | https://infratil.com/news/cdc-independent-valuation-31-march-2026/
cdc | 2026-05 | CDC signs Australia's largest-ever data centre contract: 555MW, 30-year term, US investment-grade customer; contracted capacity passes 1GW; FY27 capex A$3.8-4.2bn | CDC签澳洲史上最大合约：555MW、30年、美国投资级客户；签约破1GW | https://infratil.com/news/cdc-signs-555mw-data-centre-contract-with-us-customer/cdc-signs-555mw-data-centre-contract-with-us-customer/
cdc | 2026-07 | Infratil lifts CDC valuation to A$18.5bn (+23.6% q/q); operating leasable 550MW, 810MW under construction, 3.9GW pipeline to FY40 | Infratil上调CDC估值至185亿澳元（+23.6%）；在运550MW、在建810MW | https://www.sharecafe.com.au/2026/07/06/infratils-cdc-valuation-soars-to-a18-5-billion-on-capacity-growth/
centuria-resetdata | 2026-01 | CIP acquires Wellcamp Data Centre, Toowoomba (2.5MW, expandable) for A$30m | CIP以3000万澳元收购Toowoomba Wellcamp数据中心（2.5MW，可扩建） | https://www.datacenterdynamics.com/en/news/centuria-eyes-250mw-of-data-center-capacity-in-australia/
centuria-resetdata | 2026-06 | Centuria Industrial REIT unveils data centre strategy; CNI raises A$300m for ResetData expansion | Centuria Industrial REIT公布DC战略；CNI募资3亿澳元扩张ResetData | https://realassets.ipe.com/news/centuria-capital-raises-a300m-for-resetdata-data-centre-expansion/10137378.article
centuria-resetdata | 2026-08 | Centuria/ResetData accelerate 250MW+ pipeline: 72MW of dedicated on-site generation secured, A$165m Macquarie GPU bridge facility, CDC MSA for 7MW (LOI to 10MW) | Centuria/ResetData推进250MW+管线：72MW自备发电、1.65亿澳元GPU过桥贷 | https://www.theindustrialist.com.au/news/2026/08/13/centuria-and-resetdata-accelerate-250mw-ai-and-digital-pipeline/1786586491
dci-data-centers | 2021-01 | A$400m, 36MW SYD02 at Eastern Creek approved; A$70m ADL02 (5.4MW) in Adelaide | 4亿澳元36MW SYD02获批（Eastern Creek）；ADL02 5.4MW投7000万澳元 | https://channellife.com.au/story/dci-data-centers-to-build-400m-facility-in-sydney
dci-data-centers | 2024-06 | DCI lodges plans for 25MW CBR01 at Jerrabomberra, Canberra targeting government workloads | DCI申报堪培拉Jerrabomberra 25MW CBR01，面向政府工作负载 | https://www.datacenterdynamics.com/en/news/dci-data-centers-submits-plan-for-25mw-data-center-in-canberra-australia/
dci-data-centers | 2026-06 | Brookfield named among potential bidders for STACK's APAC data centre portfolio, which would add Melbourne scale to DCI | Brookfield列为STACK亚太资产潜在竞购方，若成交将为DCI补上墨尔本规模 | https://www.mingtiandi.com/real-estate/crelist/roundup-aip-brookfield-bid-for-stack-apac-data-centres/
digico | 2024-10 | HMC Capital agrees to acquire Global Switch Australia (Sydney East/West, Ultimo) for A$2.12bn, seeding DigiCo REIT | HMC Capital以21.2亿澳元收购Global Switch澳洲（悉尼Ultimo两座） | https://www.globalswitch.com/announcement/agreement-reached-for-the-sale-of-global-switch-australia-to-hmc-capital/
digico | 2025-10 | 14MW of new Australian customer wins; Australian contracted capacity target lifted to 41MW by June 2026; group billed 85MW by July 2026 | 新签14MW澳洲客户；澳洲签约目标上调至41MW，集团计费容量7月达85MW | https://www.datacenterdynamics.com/en/news/australias-digico-infrastructure-reit-signs-14mw-of-data-center-deals/
digico | 2026-05 | Sells Chicago CHI1 for US$750m (5% premium to cost); gearing falls to ~17%, funds SYD1 build; first 15MW of expansion completed | 7.5亿美元出售芝加哥CHI1（溢价5%），负债率降至约17%；扩建首批15MW完工 | https://www.sharecafe.com.au/2026/05/06/digico-infrastructure-reit-fortifies-balance-sheet-with-us750m-asset-sale/
digico | 2026-08 | FY26 EBITDA beats guidance; SYD1 88MW expansion brought forward | DigiCo FY26 EBITDA超指引，SYD1 88MW扩建提前 | https://www.fool.com.au/2026/08/21/digico-infrastructure-reit-posts-fy26-earnings-beat-outlines-expansion-plans/
digital-realty | 2020-11 | Digital Realty buys two 20-acre plots in Erskine Park and Horsley Park for up to 250MW | 购入Erskine Park与Horsley Park两块20英亩地，规划最高250MW | https://www.datacenterdynamics.com/en/news/digital-realty-buys-two-20-acre-plots-western-sydney-250mw-plans/
digital-realty | 2024-01 | ESR and Logos acquire Western Sydney parcels (SYD15/SYD16) once earmarked for Digital Realty expansion; DLR disputes it sold SYD15 | ESR与Logos购入原拟供Digital Realty扩建的西悉尼地块，DLR否认售出SYD15 | https://www.datacenterdynamics.com/en/news/esr-acquires-land-in-sydney-previously-set-for-digital-realty-data-center/
edge-centres | 2021-09 | Edge Centres files for Bendigo EC3; eight regional Australian sites (Grafton, Dubbo, Toowoomba, Cairns, Mackay, Townsville, Hobart, Bendigo) each with ~1MW solar and 48-hour battery | Edge Centres申报Bendigo EC3；八个区域站点各配约1MW光伏、48小时电池 | https://www.datacenterdynamics.com/en/news/edge-centres-files-permission-for-facility-in-bendigo-australia/
equinix | 2024-05 | First Australian xScale facility SY9x opens in Rosehill with PGIM Real Estate (US$575m JV, 55MW programme) | 首座澳洲xScale SY9x在Rosehill开业，PGIM合资5.75亿美元、规划55MW | https://investor.equinix.com/news-events/press-releases/detail/964/equinix-and-pgim-real-estate-open-first-xscale-data
equinix | 2024-06 | A$240m expansion of SY5 (Sydney) and ME2 (Melbourne) adds 4,175 cabinets with liquid cooling for AI | 2.4亿澳元扩建悉尼SY5及墨尔本ME2，新增4,175机柜并部署液冷 | https://newsroom.equinix.com/press-releases?item=125027
equinix | 2025-09 | Equinix selected as landing partner for the SMAP subsea cable in Perth and Sydney | Equinix获选为SMAP海缆在珀斯及悉尼的登陆合作方 | https://newsroom.equinix.com/2025-09-22-Equinix-Selected-for-SMAP-Cable-Landing-in-Perth-and-Sydney
firmus | 2025-10 | Project Southgate expanded nationally: A$73.3bn plan, 1.6GW of 'green AI factories', first 150MW (54,000 GB300 GPUs) by mid-2026 | Southgate全国计划：733亿澳元、1.6GW；首期150MW（5.4万GB300）2026年中 | https://firmus.co/newsroom/southgate-expansion
firmus | 2025-11 | A$500m equity raise at A$6bn valuation to expand Southgate from Tasmania into Melbourne, Sydney, Canberra and Perth | 以60亿澳元估值募资5亿澳元，Southgate从塔州扩至墨尔本、悉尼、堪培拉、珀斯 | https://firmus.co/newsroom/capital-raise-to-expand-project-southgate-nationally
firmus | 2026-02 | US$10bn debt financing led by Blackstone and Coatue for Project Southgate roll-out (1.6GW by 2028) | Blackstone/Coatue牵头100亿美元债务融资，Southgate 2028年达1.6GW | https://www.datacenterdynamics.com/en/news/firmus-secures-10bn-debt-financing-facility-for-project-southgate-ai-factory-roll-out/
firmus | 2026-07 | Firmus secures 600MW energy supply agreement in South Australia linked to 1.2GW of new renewables and storage; DayOne JV for 360MW campus near Singapore | Firmus签南澳600MW供电协议（配1.2GW新能源储能）；与DayOne合建360MW | https://dataxconnect.com/weekly-data-centre-news-3rd-july-2026/
fujitsu-au-dc-next-capital | 2026-06 | Reports that Fujitsu's Australian DC portfolio was being shopped in a ~A$1bn process before the smaller Next Capital deal | 此前报道Fujitsu澳洲DC组合曾以约10亿澳元寻售，最终以更小规模成交 | https://www.marketscreener.com/quote/stock/BLACKSTONE-INC-60951400/news/Fujitsu-Reportedly-Poised-to-Offload-Its-Data-Centre-Portfolio-in-1-Billion-Deal-47616955/
fujitsu-au-dc-next-capital | 2026-07 | Fujitsu sells five Australian data centres (Homebush 6MW, Greystanes 60MW site, Noble Park 12MW, Eight Mile Plains 2MW, Malaga 5MW; 25MW operational, 100MW potential) to Next Capital | Fujitsu将五座澳洲DC（在运25MW、潜力100MW）售予Next Capital | https://www.datacenterdynamics.com/en/news/fujitsu-sells-australian-data-center-business-to-next-capital/
goodman | 2026-01 | Goodman files for 90MW data centre campus in Sydney | Goodman申报悉尼90MW数据中心园区 | https://www.datacenterdynamics.com/en/news/goodman-files-to-develop-90mw-data-center-campus-in-sydney-australia-2/
goodman | 2026-03 | NSW planning pushes Goodman to secure firmed renewable PPAs for A$5.5bn Project Atlas (2029 completion) | 新州要求Goodman为55亿澳元Project Atlas锁定带保障可再生PPA（2029完工） | https://www.forbes.com.au/news/innovation/nsw-pushes-goodman-to-back-fresh-power-for-5-5-billion-ai-factory/
goodman | 2026-08 | FY26: operating profit A$2.67bn; power bank 6.4GW (3.6GW secured); data centres 78% of A$19.7bn WIP; Australian DC development partnership planned 1H FY27 | FY26经营利润26.7亿澳元；电力储备6.4GW（锁定3.6GW），DC占197亿WIP的78% | https://kalkine.com.au/news/announcements/goodman-group-reports-fy26-operating-profit-of-267-billion-data-centres-drive-wip-to-197-billion
goodman | 2026-09 | Construction starts on Project Atlas, ~A$5bn, 500MW campus at Eastern Creek, Western Sydney | 西悉尼Eastern Creek Project Atlas（约50亿澳元、500MW）开工 | https://australiatimes.com/goodman-begins-construction-on-major-sydney-data-centre-as-ai-infrastructure-boom-accelerates
google | 2021-07 | Google Cloud Melbourne region opens; A$1bn Digital Future Initiative announced | 谷歌云墨尔本区域开通；宣布10亿澳元'数字未来计划' | https://cloud.google.com/blog/products/infrastructure/the-google-cloud-region-in-melbourne-is-now-open/
google | 2026-03 | Google pauses proposed A$20bn Australian AI/data centre hub over 'permanent establishment' tax concerns; talks with Treasury continue | 谷歌因'常设机构'税务顾虑暂停200亿澳元澳洲AI枢纽计划，与财政部磋商继续 | https://ia.acs.org.au/article/2026/google-pauses--20b-australian-data-centre-investment.html
greensquaredc | 2025-03 | Partners Group acquires GreenSquareDC for ~A$1.2bn; CEO change to Charles Penny follows | Partners Group约12亿澳元收购GreenSquareDC；Charles Penny接任CEO | https://www.datacenterdynamics.com/en/news/partners-group-acquires-australian-data-center-firm-greensquaredc/
greensquaredc | 2026-01 | Sydney SYD1 (former IBM site, Western Sydney) expansion to ~110MW: 4MW upgraded to 15MW plus new 96MW building, completion Q3 2026 | 西悉尼SYD1（原IBM）扩至约110MW：4MW升至15MW，新建96MW，2026年Q3完工 | https://www.datacenterdynamics.com/en/news/australias-greensquaredc-expanding-data-center-in-greater-western-sydney/
greensquaredc | 2026-05 | Withdraws development application for 120MW WAi1 Hazelmere (Perth) after 1,836 objections and noise-assessment dispute | 撤回珀斯Hazelmere 120MW WAi1开发申请：1,836份反对及噪声评估争议 | https://bebeez.eu/2026/05/28/swiss-backed-greensquaredc-withdraws-application-for-120mw-data-center-in-perth-australia/
hmc-capital | 2024-12 | DigiCo REIT lists on ASX after A$2.4bn IPO, seeded with Global Switch Australia, iseek and YourDC | DigiCo REIT以24亿澳元IPO上市，种子资产Global Switch、iseek、YourDC | https://www.datacenterdynamics.com/en/news/australias-digico-infrastructure-reit-signs-14mw-of-data-center-deals/
hmc-capital | 2026-05 | Chicago CHI1 divested for US$750m to de-gear DigiCo | 7.5亿美元出售芝加哥CHI1，为DigiCo降杠杆 | https://www.sharecafe.com.au/2026/05/06/digico-infrastructure-reit-fortifies-balance-sheet-with-us750m-asset-sale/
hmc-capital | 2026-08 | DigiCo (managed by HMC) delivers FY26 EBITDA ahead of guidance and accelerates SYD1 | 旗下DigiCo FY26 EBITDA超指引，加快SYD1扩建 | https://www.fool.com.au/2026/08/21/digico-infrastructure-reit-posts-fy26-earnings-beat-outlines-expansion-plans/
infratil | 2026-02 | Infratil contributes A$250m of CDC's A$500m equity raise | Infratil出资2.5亿澳元参与CDC 5亿澳元增资 | https://infratil.com/news/cdc-independent-valuation-31-march-2026/
infratil | 2026-05 | FY26 result: CDC EBITDAF forecast to exceed A$1bn by FY28 (+150%) on 1GW+ contracted | FY26业绩：CDC签约超1GW，FY28 EBITDAF预计破10亿澳元（+150%） | https://infratil.com/news/infratil-full-year-results-for-the-year-ended-31-march-2026/infratil-fy2026-full-year-result-media-release/
infratil | 2026-07 | CDC stake (49.72%) valued at A$9.2bn as CDC valuation rises to A$18.5bn | Infratil所持CDC 49.72%股权估值92亿澳元，CDC整体估值升至185亿澳元 | https://www.sharecafe.com.au/2026/07/06/infratils-cdc-valuation-soars-to-a18-5-billion-on-capacity-growth/
interactive | 2025-06 | Interactive markets 100kW-per-rack high-density colocation for AI across Melbourne, Sydney and Brisbane; RE100 member | Interactive在墨尔本、悉尼、布里斯班推单柜100kW高密AI托管；加入RE100 | https://www.interactive.com.au/services/data-centres/
ispt | 2025-03 | Plans filed for 1GW Mamre Road campus in Western Sydney (State Significant Development) | 西悉尼Mamre Road 1GW园区申报州重大项目（SSD） | https://www.datacenterdynamics.com/en/news/plans-filed-for-1gw-data-center-campus-in-sydney-australia/
ispt | 2025-11 | ISPT agrees conditional sale of its approved Mamre Road, Kemps Creek data centre campus site (600MW-1GW, six buildings) to AirTrunk | ISPT有条件将已获批Mamre Road园区地块（600MW-1GW、六栋）售予AirTrunk | https://bebeez.eu/2025/11/11/airtrunk-set-to-buy-planned-1gw-data-center-site-in-western-sydney-australia/
leading-edge-dc | 2020-07 | A$19.6m Newcastle campus (1.5MW) announced with Schneider Electric prefabricated modules; Soul Pattinson-backed | Soul Pattinson支持下投1,960万澳元建Newcastle 1.5MW园区，Schneider预制模块 | https://www.datacenterdynamics.com/en/news/leading-edge-dc-pumps-13m-nsw-data-center-campus/
leading-edge-dc | 2025-06 | Six regional NSW Tier III sites operating (Newcastle, Tamworth, Dubbo, Albury, Coffs Harbour, Wagga Wagga); Victoria and Queensland flagged 'coming soon' | 新州六座区域Tier III站点在运（Newcastle至Wagga Wagga）；维州、昆州待推出 | https://leadingedgedc.com/
macquarie-data-centres | 2025-01 | Federal NRFC commits A$200m to fund IC3 Super West sovereign AI capacity | FY26 EBITDA 1.159亿澳元（+2%）；IC3 Super West锚定客户谈判进展顺利 | https://www.techpartner.news/news/macquarie-technology-group-sees-incremental-gains-in-fy26-eyes-modest-growth-in-fy27-628485
macquarie-data-centres | 2025-12 | Treasurer 'tops out' IC3 Super West (47MW, ~A$350m) at Macquarie Park | IC3 Super West（47MW、约3.5亿澳元）封顶，联邦财长出席 | https://w.media/macquarie-data-centres-tops-out-47-mw-ic3-super-west/
macquarie-data-centres | 2026-08 | FY26 EBITDA A$115.9m (+2%); IC3 Super West on track to open, anchor customer negotiations 'well progressed'; Phase 1 revenue from 2H FY27 | FY26 EBITDA 1.159亿澳元（+2%）；IC3 Super West锚定客户谈判进展顺利 | https://www.techpartner.news/news/macquarie-technology-group-sees-incremental-gains-in-fy26-eyes-modest-growth-in-fy27-628485
microsoft | 2023-10 | Earlier A$5bn commitment expands Australian sites to 29 across Sydney, Melbourne and Canberra | Nadella宣布至2029年在澳投资250亿澳元（180亿美元），DC规模扩张逾140% | https://news.microsoft.com/source/asia/features/investing-in-australias-ai-future/
microsoft | 2026-04 | Satya Nadella announces A$25bn (US$18bn) Australian investment to end-2029, expanding data centre footprint >140% | Nadella宣布至2029年在澳投资250亿澳元（180亿美元），DC规模扩张逾140% | https://news.microsoft.com/source/asia/features/investing-in-australias-ai-future/
microsoft | 2026-04 | Kemps Creek (Western Sydney) campus in advanced construction; AEMO lists 190MW connection | 西悉尼Kemps Creek园区进入施工后期，AEMO并网管线登记190MW | https://certifiedstrategic.com/insights/aemo-5-4gw-australian-data-centre-pipeline-june-2026
nextdc | 2025-12 | OpenAI and NEXTDC announce US$4.6bn Sydney AI campus partnership (S7) | OpenAI与NEXTDC宣布46亿美元悉尼AI园区合作（S7） | https://www.nextdc.com/news/building-the-next-generation-of-sovereign-ai-infrastructure-in-australia
nextdc | 2026-04 | Record 250MW single-customer commitment at S4 Horsley Park; contracted utilisation to 667MW; A$2.2bn capital plan incl. ~A$1.5bn entitlement offer | S4 Horsley Park签250MW单客户纪录大单，签约667MW；22亿澳元融资 | https://www.nextdc.com/news/record-contracted-growth-and-a2.2bn-capital-plan-to-scale-ai-ready-infrastructure
nextdc | 2026-07 | S7 Eastern Creek EIS lodged: 612MW at full build, nine buildings; OpenAI signed as anchor customer under Dec-2025 MoU | S7 Eastern Creek提交EIS：满建612MW、九栋楼，OpenAI为锚定租户 | https://www.datacenterdynamics.com/en/news/australian-stargate-data-center-in-sydney-will-offer-612mw-of-capacity/
nextdc | 2026-08 | FY26 result: contracted utilisation 740MW (+202%), built 288MW, 537MW under construction; FY27 revenue guidance A$615-640m, capex A$5.25-5.75bn | FY26签约740MW（+202%）、在建537MW；FY27资本开支52.5-57.5亿澳元 | https://www.investing.com/news/company-news/nextdc-fy26-presentation-740mw-contracted-revenue-to-jump-50-93CH-4880417
oracle | 2023-08 | Oracle launches Australian Government Cloud regions (Canberra) for sovereign workloads | Oracle推出澳洲政府云区域（堪培拉），面向主权工作负载 | https://www.datacenterdynamics.com/en/news/oracle-launches-government-cloud-region-in-australia/
oracle | 2026-03 | Oracle says it has no Australian AI data centre build plans yet; local demand is corporate/government rather than frontier-model training | Oracle称暂无在澳建AI数据中心计划，本地需求以企业/政府为主而非模型训练 | https://www.capitalbrief.com/article/oracle-is-all-in-on-ai-data-centres-just-not-in-australia-c0862544-b284-44b0-84a5-e332840e9927/
polaris | 2025-01 | Polaris continues as Springfield City Group-owned Tier III facility serving QLD government and corporate clients; no expansion announced | Springfield City Group旗下Polaris继续服务昆州政府及企业；无扩建计划 | https://www.polarisdatacentre.com.au/about-us/
stack-infrastructure | 2022-06 | STACK enters Australia with 124MW across Melbourne (Truganina), Canberra and Perth via Hickory partnership | STACK携手Hickory进入澳洲：墨尔本Truganina、堪培拉、珀斯合计124MW | https://www.globenewswire.com/news-release/2022/06/08/2459170/0/en/STACK-Infrastructure-Expands-APAC-Footprint-into-Australia-with-124MW-of-Capacity-across-Melbourne-Canberra-and-Perth.html
stack-infrastructure | 2026-06 | BlackRock-backed AIP and Brookfield among potential bidders as formal sale process prepared | BlackRock旗下AIP与Brookfield列为潜在竞购方，正式出售程序筹备中 | https://www.mingtiandi.com/real-estate/crelist/roundup-aip-brookfield-bid-for-stack-apac-data-centres/
stack-infrastructure | 2026-08 | STACK APAC portfolio (incl. Melbourne 432MW across two campuses) marketed at US$25bn+; Macquarie, GIP and IFM weighing bids | STACK亚太资产包（含墨尔本432MW）叫价250亿美元+，Macquarie/GIP/IFM有意 | https://constructionreviewonline.com/25bn-stack-apac-data-centers-draw-macquarie-bid-interest-as-ai-reshapes-construction-in-australia/
stockland | 2025-11 | NSW approves Stockland data centre at MPark innovation precinct; separate 168MW Western Sydney filing | 新州批准Stockland MPark创新区数据中心；另申报西悉尼168MW项目 | https://w.media/nsw-approves-stockland-data-centre-for-sydney-innovation-precinct/
stockland | 2026-03 | 50:50 JV with EdgeConneX finalised; MPark Macquarie Park >100MW; CEO targets 5-10% of capital to DCs (A$750m-1.5bn) | 与EdgeConneX合资落地；MPark超100MW；5-10%集团资本（7.5-15亿澳元）投DC | https://w.media/stockland-finalises-edgeconnex-data-centre-jv-as-ceo-plots-more-investment/
stockland | 2026-05 | Files for 250MW hyperscale campus at Cherry Lane, Laverton North (western Melbourne) on 35ha logistics estate | 申报墨尔本西部Laverton North 250MW超大规模园区（35公顷物流地块） | https://www.mingtiandi.com/real-estate/data-centres/stockland-seeks-approval-for-250mw-melbourne-data-centre-campus/
telstra-infraco | 2025-11 | Starwood Capital, Doma and Telstra InfraCo agree to develop 62MW AI-optimised data centre at Minchinbury, Western Sydney (early 2028) | Starwood、Doma与InfraCo合作开发西悉尼Minchinbury 62MW AI DC（2028年初） | https://www.prnewswire.com/apac/news-releases/starwood-capital-group-doma-infrastructure-group-and-telstra-infraco-announce-agreement-to-develop-62mw-ai-optimised-data-centre-in-western-sydney-302613655.html
telstra-infraco | 2026-02 | InfraCo runs three carrier-neutral DCs (St Leonards 20MW, Clayton 20MW, Deakin 4.5MW target) on a 'connectivity-first' strategy | InfraCo三座中立DC（St Leonards 20、Clayton 20、Deakin 4.5MW）'连接优先' | https://certifiedstrategic.com/insights/telstra-s-data-centre-disconnect-headcount-out-hyperscale-in
vocus | 2025-05 | ACCC does not oppose Vocus-TPG EGW deal, creating Australia's largest independent fibre network (~50,000km) | ACCC不反对Vocus收购TPG EGW，形成澳洲最大独立光纤网络（约5万公里） | https://www.accc.gov.au/media-release/vocus%E2%80%99-proposed-acquisition-of-tpg-enterprise-government-and-wholesale-business-not-opposed
vocus | 2025-08 | Vocus completes A$5.25bn acquisition of TPG Telecom's enterprise, government and wholesale fixed business incl. fibre and PPC-1 cable | Vocus完成52.5亿澳元收购TPG企业、政府及批发固网业务（含光纤和PPC-1海缆） | https://www.datacenterdynamics.com/en/news/vocus-closes-acquisition-of-tpg-telecoms-fiber-assets/
firmus | 2026-10 | Firmus and CDC end the 1.6GW Project Southgate partnership after only 42MW was deployed at CDC's Melbourne site; Firmus pivots to Asia and its own Tasmanian campuses | Firmus与CDC终止1.6GW Southgate合作，仅落地42MW | https://www.datacenterdynamics.com/en/news/firmus-and-cdc-end-16gw-project-southgate-collaboration-deploy-just-42mw/
cdc | 2026-10 | CDC walks away from the 1.6GW Firmus rollout, citing Firmus' Asian expansion and concerns over funding and scalability; seeks alternative AI partners | CDC退出与Firmus的1.6GW合作，质疑其融资与扩张能力 | https://www.datacenterdynamics.com/en/news/firmus-and-cdc-end-16gw-project-southgate-collaboration-deploy-just-42mw/
firmus | 2026-10 | Firmus prices its ASX IPO at A$11.00 per share, raising ~A$7.1bn (US$4.9bn) at an implied ~A$43.7bn; bookbuild 6-9 October, debut targeted 22-23 October - Australia's second-largest float | Firmus IPO定价11澳元，募资约71亿澳元，估值约437亿澳元 | https://www.mingtiandi.com/real-estate/crelist/roundup-australias-firmus-prices-4-9b-data-centre-ipo/
microsoft | 2026-10 | NSW approves Microsoft's A$1.26bn, 96MW IT load data centre at Honeman Close, Huntingwood in western Sydney | 新州批准微软Huntingwood项目，96MW、12.6亿澳元 | https://www.mingtiandi.com/real-estate/data-centres/microsoft-wins-approval-for-902m-sydney-data-centre/
stockland | 2026-10 | NSW approves Stockland's A$630.4m Road 1 data centre at Macquarie Park - 10 storeys, 49MW (34.3MW IT load), adjoining a 76.4MW facility approved in March | 新州批准Stockland的Macquarie Park项目，49MW、6.3亿澳元 | https://www.mingtiandi.com/real-estate/data-centres/microsoft-wins-approval-for-902m-sydney-data-centre/
cdc | 2026-09 | CDC lodges plans for a 1.4GW, up to A$15bn campus at 216 Ashfords Road, Gregadoo near Wagga Wagga NSW: four 240MW buildings on 103.4ha, 1.3km from TransGrid's Wagga Terminal Station | CDC申报Wagga Wagga 1.4GW园区，投资至多150亿澳元 | https://www.datacenterdynamics.com/en/news/australias-cdc-plans-gigawatt-scale-data-center-campus-in-wagga-wagga/
cdc | 2026-09 | ACT Territory Planning Authority grants conditional approval for CDC's 84MW, A$203.5m Beard 2 in Canberra - 12 data halls, second stage of the Beard campus alongside 39MW Beard 1 | ACT批准CDC堪培拉Beard 2项目，84MW、2.035亿澳元 | https://w.media/cdc-wins-approval-for-au203-5m-beard-2-data-centre-in-canberra/
infratil | 2026-09 | Infratil marks CDC at A$18.5bn midpoint (A$17.4-19.6bn) at 30 September; its 49.69% stake slips A$45m to A$9.168bn as a higher forward yield curve offsets stronger contracting | Infratil所持CDC股权降至91.68亿澳元，估值维持185亿澳元 | https://www.tipranks.com/news/company-announcements/infratil-reports-largely-steady-a18-5-billion-valuation-for-cdc-amid-rising-rates
hyperdc | 2026-09 | New entrant HyperDC lodges a Victorian planning permit for a 400MW campus at 715 Ballan Road, Moorabool, beside AusNet's Moorabool Terminal Station and the Victorian Big Battery | 新进入者HyperDC申报Moorabool 400MW园区 | https://www.datacenterdynamics.com/en/news/plans-filed-for-400mw-data-center-campus-outside-melbourne-australia/
centuria-resetdata | 2026-09 | Monash Council rejects Centuria's 38MW, A$137m Clayton expansion against officer advice, citing power demand, cooling noise and Victoria's proposed 150m residential buffer | Monash否决Centuria在Clayton的38MW扩建申请 | https://w.media/monash-rejects-centuria-data-centre-plans-as-victoria-tightens-planning-rules/
goodman | 2026-09 | Goodman withdraws its 90MW Project Mars application at 12 Mars Road, Lane Cove, saying the policy and regulatory environment has evolved significantly since March 2025 | Goodman撤回Lane Cove的90MW Project Mars申请 | https://www.datacenterdynamics.com/en/news/goodman-withdraws-application-for-90mw-data-center-campus-in-sydney-australia/
greensquaredc | 2026-09 | GreenSquareDC signs Sharon AI as long-term anchor for stage 1 of the 110MW SYD1 campus in Western Sydney - its first disclosed customer commitment | GreenSquareDC签下Sharon AI，锁定SYD1一期 | https://www.datacenterdynamics.com/en/news/sharon-ai-to-lease-capacity-from-australias-greensquaredc/
sharon-ai | 2026-09 | Sharon AI leases stage 1 of GreenSquareDC's SYD1 and will deploy ~8,200 NVIDIA Blackwell Ultra GPUs from Q4 2026 | Sharon AI承租GreenSquareDC SYD1一期，部署约8,200张GPU | https://www.datacenterdynamics.com/en/news/sharon-ai-to-lease-capacity-from-australias-greensquaredc/
vocus | 2026-09 | Vocus announces a 4,000km ducted Brisbane-Darwin fibre route via Townsville under its Australian Digital Infrastructure Platform: up to 3,456 strands, in service 2030 | Vocus宣布布里斯班至达尔文4,000公里光缆，2030年投运 | https://www.datacenterdynamics.com/en/news/vocus-to-build-4000km-fiber-link-between-brisbane-and-darwin/
sharon-ai | 2026-09 | Sharon AI buys the former Visy / Norske Skog paper mill at Ettamogah near Albury NSW for ~A$50m, its first owned Australian site; Visy stays on as a warehouse tenant | Sharon AI以约5,000万澳元买下Albury附近Ettamogah纸厂地块 | https://www.datacenterdynamics.com/en/news/sharonai-buys-former-printing-press-outside-albury-australia/
aws | 2026-09 | NSW approves a A$2.17bn AWS-linked data centre at 2 Glendenning Road, Glendenning: 235MW maximum electrical demand, 193.6MW IT load, over Blacktown City Council objections | 新州批准AWS关联的Glendenning项目，IT负载193.6MW | https://w.media/amazon-receives-approval-for-aud-2-17bn-sydney-data-centre/
airtrunk | 2026-09 | AirTrunk lodges an EIS for a 540MW, A$3.7bn State Significant Development at the former Hydro Aluminium smelter, Loxford near Kurri Kurri NSW, with a A$37m community package and 350+ ongoing jobs | AirTrunk申报Kurri Kurri 540MW项目，投资37亿澳元 | https://w.media/airtrunk-proposes-aud-3-7bn-nsw-data-centre-with-aud-37m-community-offer/
zerra-dc | 2026-09 | Anthropic signs Australia's first AI-lab data centre lease, anchoring stage 1 of Zerra DC's A$31.9bn Western Downs Digital Park near Dalby QLD (1.44GW planned, up to 2.16GW peak) | Anthropic锁定Zerra DC的Western Downs一期，总投资319亿澳元 | https://www.mingtiandi.com/real-estate/data-centres/anthropic-to-lease-phase-1-of-zerra-dc-queensland-data-centre/
cdc | 2026-09 | Infratil investor day: CDC at 1.1GW contracted (625MW signed since May), 350MW deployed and earning, 810MW under construction FY27-29, 3.9GW pipeline; FY27 EBITDAF guidance lifted to A$710-750m on A$3.8-4.2bn capex | CDC投资者日：签约1.1GW、在建810MW，FY27指引上调 | https://infratil.com/news/data-centre-demand-drives-growth-and-guidance-increase/infratil-investor-day-2026-cdc-update/
firmus | 2026-09 | Firmus opens its ASX IPO roadshow; Tasmanian delivery slows on Hydro Tasmania supply priority, Marinus Link delays and George Town objections to the 288MW Bell Bay proposal, pushing focus to South Australia | Firmus启动IPO路演；塔州受限于供电与Marinus Link，转向南澳 | https://www.abc.net.au/news/2026-09-16/data-centre-firmus-courting-investors-ahead-of-share-float/107154842
nextdc | 2026-09 | NEXTDC raises A$1.1bn (US$796m) of convertible notes for its development pipeline - its third capital raise in roughly four months | NEXTDC发行11亿澳元可转债，四个月内第三次融资 | https://www.datacenterdynamics.com/en/news/australias-nextdc-raises-au11bn-in-convertible-notes/

## Market
metric_id | label_en | label_zh | value | unit | notes | source | as_of | kpi | kpi_order
operational_mw | Operational IT load (national) | 全国在运IT负载 | 1450 | MW | end-2025 / FY25; ~160 facilities | Data Centres Australia / DC Byte Forecast Report Apr 2026; AEMO QED Q1-2026 | 2026-04 | TRUE | 1
operational_facilities | Operational facilities | 在运数据中心数量 | 162 | count |  | Data Centres Australia / DC Byte Apr 2026 | 2026-04 | FALSE
sydney_operational_mw | Sydney operational IT load | 悉尼在运IT负载 | 917 | MW | H1 2026, +17% y/y | Cushman & Wakefield APAC DC Update H1 2026 | 2026-08 | FALSE
aemo_connection_pipeline_mw | Grid-connection pipeline (>5 MW projects, AEMO) | AEMO并网申请管线 | 5400 | MW | 4.1 GW application + 1.3 GW implementation; NSW ~60%, VIC ~40% | AEMO Quarterly Energy Dynamics Q1 2026 | 2026-04 | TRUE | 3
announced_pipeline_mw | Announced pipeline (headline) | 公告管线总量 | 21600 | MW | 16.8 GW early-stage, 3.1 GW committed, 0.2 GW under construction | DC Byte / Data Centres Australia Apr 2026 | 2026-04 | TRUE | 5
committed_pipeline_mw | Committed pipeline | 已落实管线容量 | 3100 | MW |  | DC Byte / Data Centres Australia Apr 2026 | 2026-04 | TRUE | 7
forecast_2030_mw | Forecast operational 2030 | 2030年在运容量预测 | 3200 | MW | Sydney 2.0 GW, Melbourne 1.1 GW | DC Byte / Data Centres Australia | 2026-04 | TRUE | 8
capex_to_2030_aud_bn | Investment to 2030 (central case) | 至2030年投资（基准情形） | 150 | AUD bn | A$220bn if all announced built | CommBank economics Aug 2026 | 2026-08 | FALSE
jll_pipeline_mw | National pipeline (JLL) | 全国管线容量（JLL） | 16200 | MW | 16.2 GW across all stages | JLL, Australian data centre growth and the impacts on the industrial sector, 10 Sep 2026 | 2026-09 | FALSE
jll_pipeline_value_aud_bn | Pipeline investment value (JLL) | 管线投资额（JLL） | 155 | AUD bn | A$155bn of announced projects | JLL via Mingtiandi, 10 Sep 2026 | 2026-09 | FALSE
nsw_grid_connection_requests_mw | NSW data centre grid connection enquiries (Transgrid) | 新州数据中心并网咨询量（Transgrid） | 20000 | MW | ~2x current NSW peak demand; Sydney capacity largely committed | Transgrid via W.Media, 10 Sep 2026 | 2026-09 | TRUE | 4
nsw_dc_peak_demand_2036_mw | NSW data centre peak demand 2036f | 新州数据中心2036年峰值需求预测 | 3670 | MW | Transgrid planning forecast | Transgrid via W.Media, 10 Sep 2026 | 2026-09 | FALSE

## Reg_Jurisdictions
jurisdiction_id | name_en | name_zh | market | key_bodies | overview_en | overview_zh | sources
FED | Federal / National (NEM) | 联邦 / 国家电力市场 (NEM) | NEM (NSW, VIC, QLD, SA, TAS, ACT); national laws also apply in WA (WEM) and NT | AEMO, AER, AEMC, Energy and Climate Change Ministerial Council (ECMC), DCCEEW, National Environmental Protection Agency (NEPA, EPBC Act), Foreign Investment Review Board (FIRB)/Treasury, Cyber and Infrastructure Security Centre (Home Affairs, SOCI Act), Hosting Certification Framework (Home Affairs), National Cabinet | Large-load grid connection in the NEM sits under the National Electricity Law and NER Chapter 5 (transmission and large connections) and Chapter 5A (distribution), run by the network service provider with AEMO advising on technical standards and the AER regulating charges and investment tests. - The federal layer moved sharply in 2026: the AEMC's Package 2 access-standards rule (ERC0394, final determination due 29 October 2026) introduces tiered technical standards for inverter-based loads of 30 MW and above. - AEMO lodged ERC0455 for registration and visibility of large inverter-based loads (21 July 2026); Minister Bowen lodged two cost-recovery rule changes (Package 1 ERC0448 and Package 2, 22 July 2026). - AEMC advice to Ministers (5 August 2026): data centres should surrender REGO certificates from new generation, contract new firm capacity, register with AEMO and offer demand flexibility. - National Cabinet (26 August 2026) endorsed mandatory national data centre standards, with Commonwealth legislation expected early 2027, sitting on top of (not replacing) state planning approvals. - Separately: foreign buyers need FIRB approval (data centres are typically national security businesses under the SOCI Act); operators of critical data storage or processing assets carry SOCI Act registration, incident-reporting and risk-management duties; EPBC Act referral applies only where a matter of national environmental significance is likely to be significantly affected. | NEM内大负荷并网的法律依据是National Electricity Law及NER第5章（输电及大型接入）、第5A章（配电接入），由所属网络服务商执行，AEMO把关技术标准，AER监管接入费用与网络投资测试。 - 2026年联邦层面动作密集：AEMC第二批接入标准规则（ERC0394，最终裁定定于2026年10月29日）对30 MW及以上逆变器型负荷设分级技术标准。 - AEMO于7月21日提交ERC0455，要求大型逆变器型负荷注册并纳入可见性管理；Bowen部长7月22日提交两项成本回收规则修改（第一批ERC0448、第二批）。 - AEMC 8月5日向部长理事会建议：数据中心须注销新建电源的REGO证书、签订新增可靠容量合约、向AEMO注册并提供需求灵活性。 - 国家内阁8月26日通过全国强制性数据中心标准，联邦立法预计2027年初出台，叠加于各州规划审批之上而非取而代之。 - 另有三项联邦事项：外资买家须过FIRB（数据中心通常属SOCI Act下的国家安全业务）；关键数据存储/处理资产运营者负有SOCI Act登记、事件报告及风险管理义务；EPBC Act仅在可能对国家环境重要事项造成重大影响时触发。 | https://www.aemc.gov.au/sites/default/files/content//NER-v105-Chapter-05.PDF ¦ https://www.aemc.gov.au/rule-changes/improving-nem-access-standards-package-2 ¦ https://www.aemc.gov.au/rule-changes/cost-recovery-network-augmentations-package-1 ¦ https://www.aemc.gov.au/rule-changes/operational-integration-and-visibility-large-inverter-based-loads ¦ https://www.aemc.gov.au/news-centre/media-releases/data-centres-bring-clean-firm-energy-be-flexible-and-pay-their-way-aemc-advises-ministers ¦ https://www.aemo.com.au/newsroom/news-updates/digital-demand-surge ¦ https://www.mallesons.com/au/en/insights/latest-thinking/big-day-for-data-centres.html ¦ https://www.industry.gov.au/NationalDataCentreExpectations ¦ https://www.cisc.gov.au/information-for-your-industry/data-storage-and-processing/legislation-regulation-and-compliance/soci-act-2018 ¦ https://www.hostingcertification.gov.au/ ¦ https://www.allens.com.au/insights-news/insights/2026/05/extensive-reforms-to-the-firb-regime/ ¦ https://www.claytonutz.com/insights/2026/june/epbc-act-reforms-and-national-epa-commencing-soon-what-proponents-need-to-know-from-1-july-2026 ¦ https://www.claytonutz.com/insights/2026/august/nine-governments-one-rulebook-national-cabinet-backs-mandatory-ai-and-data-centre-standards
NSW | New South Wales | 新州 (NSW) | NEM | NSW Department of Planning, Housing and Infrastructure (DPHI), Independent Planning Commission (IPC), Infrastructure NSW, EnergyCo, Consumer Trustee (AEMO Services), Energy Security Target Monitor, Transgrid (TNSP), Ausgrid / Endeavour Energy / Essential Energy (DNSPs), NSW EPA, IPART, Sydney Water, AEMO, AER, AEMC | NSW is the tightest and most rule-intensive jurisdiction for a large data centre. - Planning: any facility over 15 MW is State Significant Development under the EP&A Act, assessed by DPHI against the NSW Data Centre Guidelines (17 August 2026) with a 75-day assessment target. - The Guidelines impose heavy performance measures: PUE/WUE limits, recycled water, 25%/2-hour demand flexibility, and 10-year PPAs with 40% wind and 4-hour storage. - Grid connection follows NER Chapter 5/5A with Transgrid or the DNSPs, but Transgrid describes Sydney-basin transmission capacity as 'largely exhausted'; its Network Capacity Allocation Policy (effective 14 August 2026) holds capacity only for ≥30 MW inverter-based loads that sign a Network Connection Agreement and meet six readiness tests within three months. - The Electricity Infrastructure Investment Amendment Bill 2026 (introduced 5 August 2026) will let the Minister declare 'large load access schemes' for ≥5 MW infrastructure. - The accompanying consultation paper proposes for ≥15 MW data centres a $30,000/MW entry bond, a Major Network Upgrade Fee of $200,000/MW (Sydney–Newcastle–Wollongong) or $100,000/MW elsewhere, take-or-pay network charges, binding demand profiles and mandated demand response; regulations are targeted for Q4 2026 and access-scheme consultation from late 2026. | 对大型数据中心而言，新州是全澳监管最严、规则最密的辖区。 - 规划：15 MW以上设施一律属EP&A Act下的SSD，由DPHI依2026年8月17日NSW Data Centre Guidelines评估，目标审批期75天。 - 指引设置了苛刻的绩效指标：PUE/WUE上限、再生水、25%/2小时需求灵活性、含40%风电及4小时储能的10年期PPA。 - 并网依NER第5/5A章与Transgrid或DNSP办理，但Transgrid称悉尼盆地输电容量“基本耗尽”；其2026年8月14日生效的Network Capacity Allocation Policy只为签署Network Connection Agreement并在三个月内通过六项准备度测试的30 MW及以上逆变器型负荷保留容量。 - Electricity Infrastructure Investment Amendment Bill 2026（8月5日提交议会）授权部长对5 MW及以上负荷设施宣布“大负荷接入计划”。 - 配套咨询文件针对15 MW及以上数据中心提出：每MW 3万澳元入门保证金、每MW 20万澳元（悉尼–纽卡斯尔–卧龙岗）或10万澳元（其他地区）的Major Network Upgrade Fee、照付不议网络费、约束性需求曲线及强制需求响应；法规拟2026年四季度出台，接入计划2026年底起咨询。 | https://www.infrastructure.nsw.gov.au/media/4jlictae/id0073_nsw-data-centre_guidelines.pdf ¦ https://www.planning.nsw.gov.au/policy-and-legislation/planning-reforms/ssd-warehouses-and-data-centres ¦ https://www.gadens.com/insights/data-centre-planning-approvals-in-new-south-wales-powering-the-future,-planning-for-the-present ¦ https://www.claytonutz.com/insights/2026/august/nsw-draws-the-line-what-the-new-data-centre-policy-framework-means-for-investors-developers-government-and-communities ¦ https://www.mallesons.com/au/en/insights/latest-thinking/another-big-day-for-data-centres-in-nsw-a-new-framework-for-connection.html ¦ https://www.energy.nsw.gov.au/nsw-plans-and-progress/regulation-and-policy/public-consultations/data-centres ¦ https://legislation.nsw.gov.au/view/pdf/bill/affe6b31-bef0-49e6-98e1-f9eac558401a ¦ https://www.transgrid.com.au/about-us/network/network-connections/data-centres-and-electricity-capacity-in-nsw/ ¦ https://w.media/transgrid-sets-six-tests-for-data-centres-seeking-nsw-grid-capacity/ ¦ https://www.transgrid.com.au/media/c0hbf1gj/20260617-update-on-network-capacity.pdf
VIC | Victoria | 维州 (VIC) | NEM (Victoria has a distinct transmission planning/connection regime: VicGrid plans and manages connections; AusNet Transmission is the Declared Transmission System Operator) | Minister for Planning / Department of Transport and Planning (Development Facilitation Program), local councils, VicGrid, AusNet (transmission DTSO and eastern DNSP), CitiPower/Powercor, Jemena, United Energy, Essential Services Commission (ESC), Energy Safe Victoria, EPA Victoria, Invest Victoria / Investment Coordinator-General, DJSIR (Sustainable Data Centre Action Plan), AEMO, AER, AEMC | Victoria has no dedicated data-centre statute; planning consent is a permit under the Planning and Environment Act 1987, normally from the local council. - Data centres are treated as a 'utility installation' type use (no bespoke VPP definition since Amendment VC159), generally permissible in Industrial 1/3 and Commercial 2 zones. - Larger projects use the Development Facilitation Program: the Minister for Planning becomes responsible authority via clause 53.22 (Significant Economic Development) with no third-party appeals; 17+ Melbourne data centre sites have been handled as ministerial permits. - Grid connection follows NER Chapter 5 for transmission (managed since 2025 by VicGrid with AusNet as DTSO, ahead of a new Victorian Access Regime in 2027) and Chapter 5A/Chapter 5 for the five DNSPs. - The Government's AI Mission Statement and $5.5 m Sustainable Data Centre Action Plan (February 2026) focus on land, energy and water coordination rather than binding rules. - Local resistance is growing (e.g. Hume City Council's August 2026 moratorium motion); AEMO puts roughly 40% of the NEM's 5.4 GW transmission-connected data centre pipeline in Victoria. | 维州没有专门的数据中心法规，规划许可依Planning and Environment Act 1987以规划许可证形式发放，通常由地方议会审批。 - 数据中心按“utility installation”类用途处理（VC159修正案后VPP无专门定义），一般可在Industrial 1/3区及Commercial 2区开发。 - 大型项目走Development Facilitation Program：规划部长依clause 53.22（Significant Economic Development）成为责任机构，无第三方上诉；墨尔本已有17个以上数据中心场址以部长许可方式处理。 - 并网方面，输电依NER第5章（2025年起由VicGrid管理、AusNet任DTSO，2027年将实施新的Victorian Access Regime），配电依第5A/5章与五家DNSP办理。 - 州政府的AI Mission Statement及550万澳元Sustainable Data Centre Action Plan（2026年2月）侧重土地、能源、水的统筹协调，不设约束性规则。 - 地方阻力上升（如Hume City Council 2026年8月的暂停动议）；AEMO估算NEM 5.4 GW输电接入数据中心管线中约40%位于维州。 | https://tract.com.au/data-centres-a-planning-perspective/ ¦ https://www.invest.vic.gov.au/explore-your-sector/digital-technology/data-centres ¦ https://djsir.vic.gov.au/priorities-and-initiatives/ai-mission-statement/sustainable-data-centre-action-plan ¦ https://www.vicgrid.com.au/industry/access-and-connections/transmission-connections-process ¦ https://www.ausnetservices.com.au/projects-and-innovation/data-centres ¦ https://www.planning.vic.gov.au/planning-approvals/ministerial-permits-register/ministerial-permits/76685df6-baaf-f011-bbd2-6045bdc32df2 ¦ https://datacentres.civicinterplay.io/sheets/vic ¦ https://www.ashurstperkinscoie.com/en/insights/australia-evolving-data-centre-landscape-policy-meets-pipeline/
QLD | Queensland | 昆州 (QLD) | NEM | Local governments (Planning Act assessment managers), State Assessment and Referral Agency (SARA), Coordinator-General (SDPWO Act), Department of State Development, Infrastructure and Planning, Powerlink (TNSP), Energex / Ergon Energy (Energy Queensland DNSPs), Queensland Department of Environment (EP Act), Trade and Investment Queensland, Queensland Data Centres Council, AEMO, AER, AEMC | Queensland has no data-centre-specific planning pathway: a data centre is assessed under the Planning Act 2016 against the local government planning scheme, with the State Assessment and Referral Agency handling state interests. - It is usually code or impact assessable as a warehouse/high-impact or 'utility installation' type use in industrial zones. - Very large projects can seek 'coordinated project' declaration from the Coordinator-General under the SDPWO Act 1971, but the August 2026 SDPWO amendments expressly exclude commercial data centres from the new 'State strategic project' fast-track. - Premier Crisafulli has said Queensland will require a social impact assessment and community benefit agreement with the local council before a data centre DA is lodged, mirroring the 2025 renewable-energy reforms. - Queensland (with the NT) secured an 'energy-agnostic' firming approach at National Cabinet, so coal and gas can back data centre load. - Grid connection follows NER Chapter 5 with Powerlink (supported by the Connections Guarantee timeframes under the Energy Roadmap) or NER Chapter 5A/5 with Energex/Ergon under the Large Customer Connection Manual (effective 5 January 2026); mega-projects such as the 2.16 GW Western Downs Digital Park near Dalby are testing the council DA route and direct Powerlink connection. | 昆州没有专门的数据中心规划路径：数据中心依Planning Act 2016按地方政府规划方案评估，州级利益由State Assessment and Referral Agency（SARA）处理。 - 通常作为仓储/高影响或“utility installation”类用途在工业区做代码评估或影响评估。 - 超大型项目可依SDPWO Act 1971申请Coordinator-General宣布为“coordinated project”，但2026年8月SDPWO修正案明确把商业数据中心排除在新设“State strategic project”快速通道之外。 - 州长Crisafulli表示，数据中心提交DA前须完成社会影响评估并与地方议会签订社区利益协议，做法沿用2025年可再生能源改革。 - 昆州（与北领地）在国家内阁争取到“能源技术中立”的可靠容量方式，煤电和燃气可为数据中心负荷提供支撑。 - 并网依NER第5章与Powerlink办理（受Energy Roadmap下Connections Guarantee时限保障），或依第5A/5章按Large Customer Connection Manual（2026年1月5日生效）与Energex/Ergon办理；达尔比附近2.16 GW的Western Downs Digital Park等巨型项目正在检验议会DA路径及直连Powerlink的可行性。 | https://www.legislation.qld.gov.au/view/pdf/inforce/current/act-2016-025 ¦ https://www.minterellison.com/articles/major-reforms-to-fast-track-projects-in-queensland ¦ https://www.powerlink.com.au/sites/default/files/2024-12/Connection%20Application%20Guide.pdf ¦ https://www.powerlink.com.au/connections-guarantee ¦ https://www.energex.com.au/__data/assets/pdf_file/0011/1090649/Large-Customer-Connection-Manual-3040635.pdf ¦ https://www.abc.net.au/news/2026-08-24/ai-data-centre-energy-rules-override-qld/107068536 ¦ https://www.abc.net.au/news/2026-09-14/western-downs-digital-park-data-centre-energy-queensland/107115082 ¦ https://www.ashurstperkinscoie.com/en/insights/australia-evolving-data-centre-landscape-policy-meets-pipeline/
WA | Western Australia | 西澳 (WA) — WEM 市场 | WEM (Wholesale Electricity Market, South West Interconnected System) – not the NEM; NER does not apply | Western Australian Planning Commission / Statutory Planning Committee, local governments, Development Assessment Panels, Department of Planning, Lands and Heritage, WA EPA / DWER, Western Power (network operator, SWIS), AEMO (WEM operator and system operator in WA), Economic Regulation Authority (ERA), Coordinator of Energy / Department of Energy and Economic Diversification (EPWA), Synergy and contestable retailers, Building and Energy (electrical safety), Horizon Power (regional) | Western Australia sits outside the NEM, so its own market and network-access law, not the NER, governs large-load connections. - The South West Interconnected System runs under the Electricity Industry Act 2004, the Wholesale Electricity Market Rules and the Electricity Networks Access Code 2004, with Western Power processing applications under its ERA-regulated Applications and Queuing Policy, Contributions Policy and Technical Rules. - Large distribution loads (≥10 MVA) and transmission loads (typically 132/330 kV) go through Western Power's major customer connection process, refreshed June 2026. - Supply comes from Synergy or a contestable retailer, which must hold Individual Reserve Capacity Requirements under the WEM's Reserve Capacity Mechanism, so a 100 MW data centre needs certified capacity locked in years ahead. - Planning consent is granted by local government or a Development Assessment Panel under the Planning and Development Act 2005, or via the permanent Significant Development Pathway (Part 11B, from 1 March 2024, ≥$20m in Perth/Peel, WAPC Statutory Planning Committee, 120-day target). - WA has no published data-centre-specific policy; a July 2026 EPWA issues paper on connections reform and Perth's subsea-cable/renewables advantages are the main state-level developments. | 西澳不属于NEM，大负荷并网依州内自有市场及网络接入法律体系办理，而非NER。 - SWIS受《2004年电力工业法》、《批发电力市场规则》及《2004年电力网络接入守则》约束，Western Power依经ERA监管的《申请与排队政策》、《分摊政策》和《技术规则》处理接入申请。 - 大型配电负荷（≥10 MVA）及输电负荷（通常132/330 kV）均走Western Power的大客户接入程序，2026年6月已更新。 - 电力由Synergy或可竞争零售商供应，零售商须依WEM备用容量机制持有个体备用容量要求，故100 MW级数据中心须提前数年锁定经认证的容量。 - 规划许可依《2005年规划与发展法》由地方政府或开发评估委员会发放，或走永久性重大开发路径（第11B部分，2024年3月1日起，珀斯/皮尔地区2000万澳元以上，由WAPC法定规划委员会以120天为目标裁定）。 - 西澳没有专门的数据中心政策；2026年7月EPWA接入改革议题文件及珀斯的海缆和可再生能源优势是主要的州级动态。 | https://www.planning.wa.gov.au/significant-development-pathway ¦ https://www.westernpower.com.au/resources-education/industry-resources/large-industry-customers-and-generators/major-customer-connection-review/ ¦ https://www.westernpower.com.au/products-services/install-something-new/connect-my-home-or-business/transmission-connected-loads-generators/ ¦ https://www.westernpower.com.au/products-services/install-something-new/connect-my-home-or-business/distribution-loads--large-generators/ ¦ https://www.wa.gov.au/system/files/2026-07/issues-paper-der-data-and-connections-reform.pdf ¦ https://www.aemo.com.au/newsroom/news-updates/digital-demand-surge ¦ https://www.ashurstperkinscoie.com/en/insights/australian-electricity-and-gas-markets-july-2026-update/
SA | South Australia | 南澳 (SA) | NEM | State Planning Commission / State Commission Assessment Panel (SCAP), council assessment panels, Coordinator-General (Office for Major Projects), Department for Housing and Urban Development (PlanSA), SA EPA, Office of the Technical Regulator (OTR), SA Water, ElectraNet (TNSP), SA Power Networks (DNSP), Essential Services Commission of SA, AEMO, AER, AEMC | South Australia is actively courting AI data centres on the strength of its roughly 75% renewable grid and A$32bn renewable pipeline. - Planning approval runs under the Planning, Development and Infrastructure Act 2016 and the Planning and Design Code; late-2025 changes routed data centres into an 'essential infrastructure' style pathway assessed by the State Planning Commission rather than councils. - The June 2026 data centre strategy ('New energy for new demand') promises a dedicated Data Centre and AI Infrastructure Act with a Coordinator-General decision pathway, mandatory SA Water supply confirmation and Technical Regulator certification of power-system compliance; the legislation had not been introduced as of September 2026, so details remain provisional. - Grid connection follows NER Chapter 5 with ElectraNet (New Customer Connection Guide, 30 March 2026, with explicit inverter-based-load and system-strength provisions) or NER Chapter 5A/5 with SA Power Networks (Manual 18, June 2026). - SA's small, inverter-dominated system means system-strength and stability studies weigh heavily on large loads, and the IREN Bundey proposal has made water access a political issue. | 南澳凭借约75%可再生能源占比的电网及320亿澳元可再生能源储备，积极招揽AI数据中心。 - 规划审批依《2016年规划、发展与基础设施法》及《规划与设计准则》办理；2025年底的调整已将数据中心导入由州规划委员会而非议会评估的“基础设施”类路径。 - 2026年6月发布的数据中心战略（“以新能源满足新需求”）承诺出台专门的《数据中心与AI基础设施法》，设立总协调官决策路径、强制SA Water供水确认及技术监管官对电力系统合规的认证；截至2026年9月立法尚未提交议会，细节仍属暂定。 - 电网接入依NER第5章与ElectraNet办理（2026年3月30日《新客户接入指南》，含明确的逆变器型负荷及系统强度条款），或依NER第5A/5章与SA Power Networks办理（2026年6月第18号手册）。 - 南澳系统规模小且以逆变器为主，系统强度及稳定性研究对大负荷影响显著，IREN在Bundey的提案已使用水问题成为政治议题。 | https://electranet.com.au/wp-content/uploads/2026/04/New-Customer-Connection-Guide-V1.pdf ¦ https://electranet.com.au/services/connection-journey/ ¦ https://www.sapowernetworks.com.au/public/download.jsp?id=337829 ¦ https://w.media/south-australia-proposes-dedicated-data-centre-legislation/ ¦ https://www.abc.net.au/news/2026-06-23/sa-push-for-ai-data-centres-in-sa-in-new-strategy/106830536 ¦ https://www.ashurstperkinscoie.com/en/insights/australia-evolving-data-centre-landscape-policy-meets-pipeline/ ¦ https://www.pv-tech.org/green-steel-data-centres-and-hydrogen-push-south-australias-electricity-demand-toward-50twh-by-2040/
TAS | Tasmania | 塔州 (TAS) | NEM (Tasmanian region, connected via Basslink; Marinus Link under construction) | Local planning authorities (councils) and Tasmanian Planning Commission, Minister for Planning (Major Projects), Office of the Coordinator-General, EPA Tasmania (EMPCA), TasNetworks (combined TNSP and DNSP), Hydro Tasmania, Office of the Tasmanian Economic Regulator, TasWater, AEMO, AER, AEMC | Tasmania markets 100% renewable supply, cool climate and low disaster risk to data centre and AI-compute proponents. - The Coordinator-General's pipeline, revealed 9 September 2026, holds six confidential proposals totalling up to 705 MW, on top of Firmus Technologies' 444 MW public Southgate program. - Planning consent is a council permit under the Land Use Planning and Approvals Act 1993 and the Tasmanian Planning Scheme, or, for large or multi-council projects, the Major Projects pathway (LUPAA Division 2A), where the Minister declares the project and an independent Development Assessment Panel decides. - Environmental assessment of Level 2 activities sits with EPA Tasmania under EMPCA 1994. - TasNetworks is both TNSP and DNSP, so a single NER Chapter 5 process applies to transmission loads, and it requires land, planning approvals, supplier selection, Board approvals and financial close before treating a load as committed. - On 7 September 2026 the Government released Draft Expectations for Data Centres and AI Infrastructure Developers (consultation to 12 October 2026), requiring proponents to support additional renewable generation, meet their share of network/connection costs and protect grid security; the policy is non-binding for now, and critics want it given statutory force. | 塔州以100%可再生供电、凉爽气候及低灾害风险向数据中心及AI算力业主推介。 - 总协调官项目储备（2026年9月9日曝光）包含六个保密提案，合计最多705 MW，另有Firmus Technologies公开的444 MW Southgate计划。 - 规划许可依《1993年土地利用规划与审批法》及《塔州规划方案》以议会许可形式发放，或对大型或跨议会项目走重大项目路径（LUPAA第2A分部），由部长宣布项目并由独立开发评估委员会裁定。 - 二级活动的环境评估依《1994年环境管理与污染控制法》由塔州EPA负责。 - TasNetworks兼为TNSP和DNSP，输电负荷因此适用单一的NER第5章程序；TasNetworks要求在土地、规划批准、供应商选择、董事会批准及融资关闭完成后，才将负荷视为已承诺。 - 2026年9月7日州政府发布《数据中心与AI基础设施开发商期望草案》（咨询至10月12日），要求业主支持新增可再生发电、承担应分摊的网络/接入成本并保护电网安全；该政策目前不具约束力，批评者呼吁赋予法定效力。 | https://www.premier.tas.gov.au/latest-news/2026/september/clear-expectations-for-data-centres-and-ai-infrastructure ¦ https://engage.building.tas.gov.au/draft-expectations-data-centres-and-ai-infrastructure-developers ¦ https://www.examiner.com.au/story/9346904/secret-tassie-ai-data-centre-plans-exposed-in-new-document/ ¦ https://www.abc.net.au/news/2026-09-09/six-new-confidential-data-centre-proposals-tasmania-revealed/107131974 ¦ https://www.tasnetworks.com.au/connections/connections-content/transmission-connections/transmission-load-connections-process ¦ https://www.tasnetworks.com.au/Documents/Manual-documents/Transmission/Guide-to-Transmission-Connections ¦ https://www.cg.tas.gov.au/investment_opportunities/sector_opportunities/emerging_sectors/data_centres
ACT | Australian Capital Territory | 首都领地 (ACT) | NEM (part of the NSW region; ACT has no separate transmission planner – Transgrid supplies Canberra at 330/132 kV, Evoenergy is the DNSP) | Territory Planning Authority (ACT Planning), Minister for Planning, Chief Minister, Treasury and Economic Development Directorate (CMTEDD), Evoenergy (DNSP), Transgrid (TNSP, NSW), ACT EPA (Environment Protection Act 1997), Icon Water, Independent Competition and Regulatory Commission (ICRC), Access Canberra (electrical safety), AEMO, AER, AEMC | The ACT is a small but strategically important market, home to Commonwealth-facing 'Certified Strategic' facilities and already 100% renewable, so its regulatory questions concern siting and grid headroom rather than energy sourcing. - Facilities such as CDC, Macquarie and NEXTDC hold Commonwealth-facing 'Certified Strategic' status, and the Territory already sources 100% renewable electricity through territory-wide contracts. - Planning consent is a development approval under the Planning Act 2023 and Territory Plan 2023 (an outcomes-focused system commenced 27 November 2023), with the Territory Planning Authority as decision-maker and a Territory Priority Project route for major proposals. - On 26 August 2026 the Chief Minister announced an ACT Data Centre Framework: data centres confined to zones already permitting them (commercial, industrial, transport/services and some non-urban zones, never residential), a requirement to offset additional electricity demand with new renewable generation, best-practice water efficiency, and identification of preferred corridors; a draft Framework with locations and assessment criteria is due in early 2027. - Grid connection is via Evoenergy under NER Chapter 5A/5 at 11/132 kV; anything beyond Evoenergy's 132 kV supply points requires Transgrid works in NSW, so the ACT effectively inherits NSW's transmission-capacity constraints and Transgrid's capacity allocation policy for ≥30 MW loads. | 首都领地市场规模虽小但战略地位重要，聚集了面向联邦政府的“认证战略级”设施，且已实现100%可再生供电，其监管重点因此在于选址和电网裕度，而非能源来源。 - CDC、Macquarie、NEXTDC等设施持有面向联邦政府的“认证战略级”资格，全领地已通过合约实现100%可再生用电。 - 规划许可依《2023年规划法》和《2023年领地规划》（以结果为导向的体系，2023年11月27日生效）以开发批准形式发放，由领地规划局决定，重大提案可走领地优先项目路径。 - 2026年8月26日首席部长宣布《首都领地数据中心框架》：数据中心限于现行允许的分区（商业、工业、交通/服务及部分非城市区，绝不允许住宅区），须以新建可再生发电抵消新增电力需求，采用最佳实践用水效率并确定优先走廊；含选址及评估标准的框架草案预计2027年初发布。 - 电网接入通过Evoenergy依NER第5A/5章在11/132 kV办理；超出Evoenergy 132 kV供电点能力的部分需在新州境内由Transgrid施工，故首都领地实际上继承了新州的输电容量约束及Transgrid针对30 MW及以上负荷的容量分配政策。 | https://www.cmtedd.act.gov.au/open_government/inform/act_government_media_releases/barr/2026/providing-a-clear-framework-for-data-centres-in-the-act ¦ https://www.abc.net.au/news/2026-08-23/act-data-centre-policy-already-aligned-with-national-ai-standard/106936530 ¦ https://www.evoenergy.com.au/Future-energy/Network-projects ¦ https://www.hostingcertification.gov.au/ ¦ https://www.transgrid.com.au/about-us/network/network-connections/data-centres-and-electricity-capacity-in-nsw/
NT | Northern Territory | 北领地 (NT) | NT (Darwin–Katherine Interconnected System; Interim NT Electricity Market (I-NTEM) operated by NTESMO) – not the NEM; modified NER applies to network regulation only | Development Consent Authority / Minister for Planning (Planning Act 1999), Territory Coordinator (Territory Coordinator Act 2025), NT EPA (Environment Protection Act 2019), Power and Water Corporation (network operator), Northern Territory Electricity System and Market Operator (NTESMO), Utilities Commission of the NT, Territory Generation, Jacana Energy and licensed retailers, Department of Mining and Energy, AER (network revenue only) | The Northern Territory sits outside the NEM, and its tiny system size makes large data centres effectively self-generation projects. - The Darwin–Katherine system (roughly 500 MW peak) is run by NTESMO under the Interim NT Electricity Market; network access is governed by the Electricity Networks (Third Party Access) Act 2000 and Network Access Code, with the Utilities Commission as regulator, and Power and Water Corporation's Network Technical Code sets connection requirements. - The AER regulates Power and Water's network revenue under a modified NER, but NER Chapter 5 connection rules do not apply as they do in the NEM. - Any load above 2 MW (or 10% of local network capacity) uses Power and Water's major customer connection process, with NTESMO and Utilities Commission approvals needed before a connection agreement is finalised. - Because system size is tiny relative to hyperscale proposals — Beetaloo Digital's 2 GW Weddell campus would use six times the Top End's annual consumption — large data centres are effectively self-generation projects (on-site gas or hybrid) with the grid as backup, and NT, with Queensland, secured an energy-agnostic approach at National Cabinet. - Planning consent is a development permit under the Planning Act 1999 and NT Planning Scheme 2020, with the Territory Coordinator Act 2025 offering a significant-project fast-track; there is no published NT data centre policy, only ad hoc land and exclusivity deals. | 北领地不属于NEM，且系统规模极小，使大型数据中心实际上成为自发电项目。 - 达尔文–凯瑟琳系统（峰值约500 MW）由NTESMO依临时北领地电力市场运营；网络接入受《2000年电力网络（第三方接入）法》及《网络接入守则》约束，由公用事业委员会监管，Power and Water Corporation的《网络技术守则》设定接入要求。 - AER依经修改的NER监管Power and Water的网络收入，但NER第5章接入规则不像在NEM中那样适用。 - 任何超过2 MW（或占当地网络容量10%）的负荷均须通过Power and Water的大客户接入程序，且在最终签订接入协议前须取得NTESMO及公用事业委员会批准。 - 由于系统规模相对超大规模提案极小——Beetaloo Digital在Weddell拟建的2 GW园区用电量将达北端地区年用电量的六倍——大型数据中心实际上是自发电项目（现场燃气或混合供电），电网仅作备用；北领地与昆州已在国家内阁争取到能源技术中立方式。 - 规划许可依《1999年规划法》及《2020年北领地规划方案》以开发许可形式发放，《2025年领地协调官法》提供重大项目快速通道；北领地没有公开发布的数据中心政策，仅有个案性的土地及独家权安排。 | https://www.powerwater.com.au/developers/power/major-customer-connections ¦ https://www.powerwater.com.au/development/power/technical-code-and-planning-criteria ¦ https://www.powerwater.com.au/__data/assets/pdf_file/0026/354383/Major-connections-processing-agreement-template.pdf ¦ https://www.aer.gov.au/system/files/PWC%20-%208.62%20-%20Connection%20Policy%20-%2031%20Jan%2023%20-%20Public.pdf ¦ https://ntindependent.com.au/nt-government-backs-proposed-2gw-data-centre-at-weddell/ ¦ https://www.abc.net.au/news/2026-07-22/beetaloo-digital-energy-ai-hyperscale-data-centre-40-billion/106943690 ¦ https://www.abc.net.au/news/2026-07-13/data-centre-hyperscalers-target-northern-territory/106898282 ¦ https://utilicom.nt.gov.au/

## Reg_Steps
jurisdiction_id | step_no | title_en | title_zh | detail_en | detail_zh | authority | legal_basis | typical_duration | overlap_with | overlap_note_en | overlap_note_zh | sources
FED | 1 | Foreign investment approval (FIRB) and national data centre expectations screening | FIRB外资审批及全国数据中心期望筛查 | A foreign person acquiring or developing a data centre (land plus operating business) will generally need a no-objection notification under the Foreign Acquisitions and Takeovers Act 1975. - A data centre that is, or will be, a SOCI Act critical infrastructure asset is a 'national security business' with a nil monetary threshold; foreign government investors face nil thresholds in any case. - Treasury's updated Foreign Investment Policy assesses data centre investments against the Government's Expectations of Data Centres and AI Infrastructure Developers (23 March 2026: national interest, energy transition, water, skills, local capability). - Statutory decision period is 30 days plus a 10-day notification period, extendable. - The May 2026 reform package targets 30-day decisions for low-risk cases from 1 January 2027, to be enacted by legislative amendment (exposure draft not expected before late 2026). - Transgrid's NSW capacity allocation policy now lists FIRB approval among the readiness criteria for retaining transmission capacity. | 外资收购或开发数据中心（土地连同运营业务），一般须依Foreign Acquisitions and Takeovers Act 1975取得无异议通知。 - 属于或将成为SOCI Act关键基础设施资产的数据中心构成“国家安全业务”，审查金额门槛为零；外国政府投资者一律零门槛。 - 财政部更新的Foreign Investment Policy规定，数据中心投资须对照政府2026年3月23日发布的数据中心及AI基础设施开发商期望评估：国家利益、能源转型、用水、技能、本地能力。 - 法定审批期30天，另加10天通知期，可延长。 - 2026年5月改革方案：自2027年1月1日起低风险案件30天内决定，需修法落实，草案预计不早于2026年底。 - Transgrid新州容量分配政策已把FIRB批准列入保留输电容量的准备度标准。 | Treasurer / FIRB (Treasury); Department of Industry, Science and Resources (Expectations) | Foreign Acquisitions and Takeovers Act 1975 (Cth) ss 55B–55D (national security business), Foreign Acquisitions and Takeovers Regulation 2015 reg 8AA; Australia's Foreign Investment Policy (2026 update) | 30 days statutory + extensions; 3–6 months common for sensitive cases | NSW, VIC, QLD, WA, SA, TAS, ACT, NT | FIRB runs in parallel with state planning and land acquisition; state land-transfer duties and foreign-purchaser surcharges are separate state matters, and NSW's Transgrid policy makes FIRB approval a condition of keeping allocated grid capacity. | FIRB审批与州规划审批、土地收购同步推进；州级土地转让税及外国买家附加税另行处理，而新州Transgrid政策把FIRB批准作为保留已分配电网容量的前提。 | https://www.allens.com.au/insights-news/insights/2026/05/extensive-reforms-to-the-firb-regime/ ¦ https://www.industry.gov.au/NationalDataCentreExpectations ¦ https://w.media/transgrid-sets-six-tests-for-data-centres-seeking-nsw-grid-capacity/
FED | 2 | Commonwealth environmental referral (EPBC Act) where a matter of national environmental significance may be affected | EPBC Act联邦环境评估转介 | Commonwealth approval is needed only if the project is likely to significantly impact a matter of national environmental significance (listed threatened species/communities, wetlands, heritage, etc.) or is on Commonwealth land. - Most brownfield industrial sites do not trigger a referral; greenfield campuses and associated transmission lines sometimes do. - The proponent self-assesses and, if in doubt, refers the action; the Minister/NEPA decides within 20 business days whether it is a 'controlled action' and selects an assessment pathway (often preliminary documentation or a state-accredited process under a bilateral agreement). - From 1 July 2026 the reformed EPBC Act established the National Environmental Protection Agency (NEPA) as independent regulator, introduced National Environmental Standards and higher penalties, and allows 'minor or preparatory works' to be agreed during assessment. - Timing depends heavily on pathway: 3–6 months for non-controlled actions, 12–24 months for full assessment. | 仅当项目可能对国家环境重要事项（列名受威胁物种/群落、湿地、遗产等）造成重大影响，或位于联邦土地上，才需联邦审批。 - 多数棕地工业场址不触发转介；绿地园区及配套输电线路偶有触发。 - 业主先行自评，存疑则转介；部长/NEPA在20个工作日内认定是否为“受控行为”并选定评估路径，常见为初步文件评估或依双边协议认可的州程序。 - 2026年7月1日起EPBC Act改革生效：设立独立监管机构NEPA，引入国家环境标准、加重罚则，并允许在评估期间协商“小型或前期工程”。 - 周期取决于路径：非受控行为3–6个月，完整评估12–24个月。 | Minister for the Environment / National Environmental Protection Agency (NEPA) | Environment Protection and Biodiversity Conservation Act 1999 (Cth) Part 7 (referral, ss 68–75) and Part 8 (assessment), as amended by the 2025 reform package commencing 1 July 2026 | 20 business days for controlled-action decision; 3–24 months overall depending on pathway | NSW, VIC, QLD, WA, SA, TAS, ACT, NT | Where a bilateral assessment agreement applies, the state EIS/EES process is used to satisfy the Commonwealth assessment, but the Commonwealth approval decision remains separate from the state consent. | 适用双边评估协议时，可借用州的EIS/EES程序完成联邦评估，但联邦审批决定与州开发许可仍是两道独立关口。 | https://www.claytonutz.com/insights/2026/june/epbc-act-reforms-and-national-epa-commencing-soon-what-proponents-need-to-know-from-1-july-2026 ¦ https://www.kwm.com/au/en/insights/latest-thinking/epbc-act-reform-a-new-era-of-commonwealth-environmental-regulation-commencing-in-2026.html
FED | 3 | Connection enquiry and response (NER cl 5.3.2–5.3.3) | 接入咨询及NSP回复（NER第5.3章） | The Connection Applicant lodges a connection enquiry with the Network Service Provider (TNSP for transmission, DNSP for distribution) identifying site, maximum demand (MW/MVA), load type (inverter-based load), staging and target energisation date. - Under cl 5.3.3 the NSP must acknowledge within 5 business days. - The NSP's response sets out feasible connection points, indicative augmentation, technical requirements (Schedule 5.3 automatic access standards and, for large inverter-based loads, the new IBL standards from ERC0394), information needed for an application and indicative fees. - The response is due within 30 business days of enquiry fees being paid (40 business days where dedicated connection assets are involved). - Powerlink's Connections Guarantee and Energex's manual reflect these statutory timings. - AEMO's 'Digital demand surge' update targets roughly two years from application to energisation for large loads. | 接入申请人向网络服务商（输电为TNSP，配电为DNSP）提交接入咨询，载明场址、最大需求（MW/MVA）、负荷类型（逆变器型负荷）、分期安排及目标送电日期。 - 依cl 5.3.3，NSP须在5个工作日内确认收到。 - 回复内容包括可行接入点、初步增容方案、技术要求（Schedule 5.3自动接入标准，大型逆变器型负荷另加ERC0394新标准）、申请所需资料及费用估算。 - 回复期限为缴纳咨询费后30个工作日，涉及专用接入资产时为40个工作日。 - Powerlink的Connections Guarantee与Energex手册均沿用上述法定时限。 - AEMO在Digital demand surge更新中提出，大负荷从申请到送电目标约两年。 | Transmission or Distribution Network Service Provider (TNSP/DNSP) | NER cl 5.3.2 (connection enquiry), cl 5.3.3 (response to connection enquiry), cl 5.3.1A (network connection process for load); Schedule 5.3 (conditions for connection of Customers) | 30–40 business days for NSP response; enquiry phase overall 2–4 months | NSW, VIC, QLD, SA, TAS, ACT | The NER enquiry runs in parallel with (and is usually lodged before) state planning applications; in NSW, Transgrid now requires ≥30 MW applicants to show planning approval and land control before it will keep capacity allocated. | NER接入咨询与州规划申请并行，且通常先于规划申请提交；在新州，Transgrid要求30 MW及以上申请人先证明已获规划批准并控制土地，才继续保留容量。 | https://www.aemc.gov.au/sites/default/files/content//NER-v105-Chapter-05.PDF ¦ https://www.powerlink.com.au/connections-guarantee ¦ https://www.energex.com.au/__data/assets/pdf_file/0011/1090649/Large-Customer-Connection-Manual-3040635.pdf ¦ https://www.aemo.com.au/newsroom/news-updates/digital-demand-surge
FED | 4 | Application to connect, performance standards and AEMO advisory matters (NER cl 5.3.4, 5.3.4A) | 接入申请、性能标准及AEMO咨询事项 | The applicant submits a formal application to connect under cl 5.3.4 with the Schedule 5.4/5.5 information and pays the application fee. - Information includes single-line diagrams, load characteristics, harmonics and flicker data, protection and control, and for inverter-based loads PSS/E and PSCAD models. - The applicant proposes performance standards for each Schedule 5.3 requirement (e.g. S5.3.5 power factor; S5.3.11 for IBL-related matters as cited by ElectraNet). - Where an automatic access standard cannot be met, a 'negotiated access standard' is agreed under cl 5.3.4A; AEMO advisory matters require AEMO's agreement, and AEMO assesses system strength or stability impacts where relevant. - The AEMC's draft ERC0394 rule (12 March 2026) lifts the large-IBL threshold from 5 MW to 30 MW and adds disturbance ride-through and instability detection standards at or above that size; AEMO is issuing interim guidelines ahead of the final rule (due 29 October 2026). - Powerlink notes the application stage runs 'notionally 12–18 months' for complex projects. | 申请人依cl 5.3.4提交正式接入申请，附Schedule 5.4/5.5规定的资料并缴纳申请费。 - 资料包括单线图、负荷特性、谐波与闪变数据、保护与控制方案；逆变器型负荷还须提供PSS/E及PSCAD模型。 - 申请人须逐项对Schedule 5.3要求提出性能标准，如S5.3.5功率因数、ElectraNet引用的S5.3.11逆变器型负荷条款。 - 无法满足自动接入标准的，依cl 5.3.4A协商“协商接入标准”；AEMO咨询事项须经AEMO同意，必要时AEMO另评估系统强度与稳定性影响。 - AEMC ERC0394规则草案（2026年3月12日）将大型逆变器型负荷门槛由5 MW提至30 MW，并对该规模以上设施新增扰动穿越及失稳检测标准；最终规则定于10月29日，AEMO先行发布过渡指引。 - Powerlink提示，复杂项目的申请阶段“名义上需12–18个月”。 | TNSP/DNSP with AEMO (advisory matters under cl 5.3.4A) | NER cl 5.3.4 (application for connection), cl 5.3.4A (negotiated access standards), Schedules 5.3, 5.4 and 5.5; AEMC ERC0394 draft rule (new large-IBL standards in Schedule 5.3) | 6–18 months including technical studies | NSW, VIC, QLD, SA, TAS, ACT | State planning consent is typically required or well advanced before an NSP will finalise performance standards; NSW's proposed regulations would also require binding demand profiles and demand-flexibility terms to be embedded in the connection application. | NSP一般要等州规划许可已取得或接近取得，才会敲定性能标准；新州拟议法规还要求把约束性需求曲线及需求灵活性条款直接写入接入申请。 | https://www.aemc.gov.au/rule-changes/improving-nem-access-standards-package-2 ¦ https://www.aemc.gov.au/news-centre/media-releases/aemc-proposes-new-grid-standards-data-centre-connections ¦ https://electranet.com.au/wp-content/uploads/2026/04/New-Customer-Connection-Guide-V1.pdf ¦ https://www.powerlink.com.au/sites/default/files/2024-12/Connection%20Application%20Guide.pdf
FED | 5 | Offer to connect and connection agreement (NER cl 5.3.5–5.3.7); augmentation cost allocation | 接入报价、接入协议与增容成本分担 | Within 4 months of a complete application (or an agreed longer period) the NSP must make an offer to connect (cl 5.3.6), after which the parties finalise a connection agreement (cl 5.3.7). - The offer covers connection assets, any shared-network augmentation, charges, security and performance standards. - Connection assets and 'dedicated connection assets' are user-funded negotiated services (Chapter 6A Part D for transmission; Chapter 5A Part E and AER connection charge guidelines for distribution capital contributions). - Shared-network augmentation triggered by a load may be recovered through regulated revenue if it passes the RIT-T (cl 5.16) or RIT-D (cl 5.17). - Minister Bowen's July 2026 cost-recovery rule changes (ERC0448 and Package 2) target exactly this gap: data centres to pay for transmission augmentation, post prudential support and be excluded from regulated asset bases where assets strand. - Transgrid's August 2026 policy allocates capacity only on signing a (conditional or standard) Network Connection Agreement, with five readiness criteria to be met within three months. - 24 September 2026: the AEMC initiated both cost-recovery rule changes (ERC0448 Package 1 and Package 2) on a single consultation paper - submissions close 5 November 2026, draft determination 1 April 2027, completion 22 July 2027, so NER cost allocation is unchanged until mid-2027. | NSP须在收到完整申请后4个月内（或双方约定的更长期限）发出接入报价（cl 5.3.6），随后双方签署接入协议（cl 5.3.7）。 - 报价涵盖接入资产、共享网络增容、费用、担保及性能标准。 - 接入资产及“专用接入资产”属用户付费的协商服务：输电依Chapter 6A Part D，配电资本分摊依Chapter 5A Part E及AER接入费用指引。 - 负荷引发的共享网络增容若通过RIT-T（cl 5.16）或RIT-D（cl 5.17），可纳入受监管收入回收。 - Bowen部长2026年7月的成本回收规则修改（ERC0448及第二批）正针对这一缺口：数据中心承担输电增容费用、提供审慎担保，资产搁浅时不得计入受监管资产基础。 - Transgrid 2026年8月政策规定，仅在签署（有条件或标准）Network Connection Agreement后才分配容量，并须在三个月内满足五项准备度标准。 - 2026年9月24日，AEMC以一份合并咨询文件同时启动ERC0448（第一批）与第二批成本回收规则修改：意见征集至11月5日，初步裁定2027年4月1日，2027年7月22日完成；在此之前NER成本分摊维持现状。 | TNSP/DNSP; AER (RIT-T/RIT-D, connection charge guidelines); AEMC (pending cost-recovery rules) | NER cl 5.3.5 (preparation of offer), 5.3.6 (offer to connect), 5.3.7 (finalisation of connection agreement); cl 5.16 RIT-T, cl 5.17 RIT-D; Chapter 6A Part D negotiated transmission services; Chapter 5A Part E connection charges; AEMC ERC0448 (cost recovery Package 1, lodged 22 July 2026, pending) | 4 months statutory for offer; 6–12 months to executed agreement in practice | NSW, VIC, QLD, SA, TAS, ACT | NSW is legislating a state overlay (Electricity Infrastructure Investment Amendment Bill 2026) that derogates from the NER to impose entry bonds, upgrade fees and take-or-pay terms on ≥15 MW data centres; elsewhere the NER cost allocation applies unmodified. | 新州正以Electricity Infrastructure Investment Amendment Bill 2026建立州级叠加机制，偏离NER对15 MW及以上数据中心加征入门保证金、升级费及照付不议条款；其他州仍原样适用NER成本分担规则。 | https://www.aemc.gov.au/rule-changes/cost-recovery-network-augmentations-package-1 ¦ https://www.mallesons.com/au/en/insights/latest-thinking/big-day-for-data-centres.html ¦ https://www.transgrid.com.au/about-us/network/network-connections/data-centres-and-electricity-capacity-in-nsw/ ¦ https://www.aemc.gov.au/sites/default/files/content//NER-v105-Chapter-05.PDF
FED | 6 | AEMO registration / market participation decision (Chapter 2) and retailer (FRMP) arrangements | AEMO注册、市场参与及FRMP零售安排 | Today most data centres are supplied by a retailer acting as Market Customer and Financially Responsible Market Participant (FRMP) for the connection point, so the data centre itself is not registered with AEMO. - Alternatively a data centre may register as a Market Customer (cl 2.3.4) to buy directly from the spot market, or classify its load as a scheduled load (cl 2.3.4(e)/3.8) if it wishes to be dispatched. - The AEMC's 5 August 2026 advice recommends that data centres above a size threshold become registered market participants (24–36 months after ministerial endorsement). - AEMO's ERC0455 request (21 July 2026) seeks registration/visibility obligations for large inverter-based loads. - Under the draft ERC0394 rule, non-registered ≥30 MW loads must still be bound to performance standards through connection-agreement terms. - Retail contracts also become the compliance vehicle for the proposed REGO and firm-capacity obligations. | 现阶段多数数据中心由零售商供电，零售商同时是接入点的Market Customer和FRMP，数据中心本身无需向AEMO注册。 - 数据中心也可自行注册为Market Customer（cl 2.3.4）直接在现货市场购电，或将负荷归类为可调度负荷（cl 2.3.4(e)/3.8）参与调度。 - AEMC 8月5日建议：超过规模门槛的数据中心应成为注册市场参与者，部长认可后24–36个月落地。 - AEMO的ERC0455申请（2026年7月21日）寻求对大型逆变器型负荷设定注册/可见性义务。 - 依ERC0394草案，未注册的30 MW及以上负荷仍须通过接入协议条款受性能标准约束。 - 零售合同还将成为拟议REGO及可靠容量义务的履约载体。 | AEMO (registration); AEMC (rule changes); retailer as FRMP | NER Chapter 2 cl 2.3.1 (Customers), 2.3.4 (Market Customers, scheduled loads), cl 3.8 (central dispatch); AEMC ERC0455 (operational integration and visibility of large IBLs, pending); AEMC Data centre advice to ECMC (5 Aug 2026) | AEMO registration 4–12 weeks once documentation complete; retailer contracting 3–9 months | NSW, VIC, QLD, SA, TAS, ACT | The NSW Guidelines (PM 13) and proposed regulations require the PPA/firming terms and 25%/2-hour demand-flexibility capability to be evidenced in the planning and connection process, pre-empting the national REGO/firm-capacity obligations. | 新州指引（PM 13）及拟议法规要求在规划与接入环节即证明PPA/可靠容量安排及25%/2小时需求灵活性能力，实际上先于全国REGO/可靠容量义务落地。 | https://www.aemc.gov.au/news-centre/media-releases/data-centres-bring-clean-firm-energy-be-flexible-and-pay-their-way-aemc-advises-ministers ¦ https://www.aemc.gov.au/rule-changes/operational-integration-and-visibility-large-inverter-based-loads ¦ https://www.aemc.gov.au/news-centre/media-releases/aemc-proposes-new-grid-standards-data-centre-connections
FED | 7 | Metering, NMI creation and market systems (NER Chapter 7) | 计量、NMI与市场系统（NER第7章） | Before energisation the FRMP appoints a Metering Coordinator and a type 1–4 metering installation is installed, tested and registered in AEMO's MSATS with a National Metering Identifier (NMI). - A site above 100 GWh/yr typically uses type 1 or 2 metering, with current-transformer/voltage-transformer metering at the connection point. - Metering provision is contestable. - DNSPs such as Energex confirm a connection point cannot be energised until a FRMP is nominated and metering documentation is provided. - Where the site has embedded generation or storage, bidirectional metering and, if exporting, generator registration or exemption issues must also be settled. | 送电前由FRMP指定Metering Coordinator，在接入点安装、测试1–4类计量装置，并在AEMO的MSATS系统中登记取得NMI。 - 年用电量超过100 GWh的场址通常采用1类或2类计量，接入点配置CT/VT计量。 - 计量服务可竞争提供。 - Energex等DNSP明确：未指定FRMP并提交计量文件前，接入点不得送电。 - 场址若含嵌入式发电或储能，还需解决双向计量；若有外送电，须处理发电注册或豁免事宜。 | FRMP/retailer and Metering Coordinator; AEMO (MSATS); NSP | NER Chapter 7 (metering), cl 7.8 (metering installation types), MSATS Procedures | 4–12 weeks, in parallel with construction |  | Metering is a purely national (NER) matter; states add no separate approval, though the NSW proposal would use metering data to police binding demand profiles. | 计量纯属NER层面的全国事项，各州不另设审批；但新州提案拟利用计量数据监督约束性需求曲线的履行。 | https://www.energex.com.au/__data/assets/pdf_file/0011/1090649/Large-Customer-Connection-Manual-3040635.pdf
FED | 8 | Commissioning, energisation and ongoing compliance (NER cl 5.7–5.8, Schedule 5.5); SOCI Act obligations | 调试送电、持续合规及SOCI Act义务 | The NSP and applicant agree a commissioning program under the connection agreement; the NSP inspects and tests connection assets (cl 5.7). - For large inverter-based loads, ERC0394 and AEMO's interim guidelines contemplate model validation and disturbance ride-through testing akin to generator R2 testing before full load is released; staged ramp-up over 5–10 years is typical. - Once operating, a commercial data centre storing or processing business-critical data for governments or other critical infrastructure operators is a 'critical data storage or processing asset' under the Security of Critical Infrastructure Act 2018. - The responsible entity must register on the Register of Critical Infrastructure Assets within 6 months of becoming an asset, report cyber incidents (12 hours for significant, 72 hours for other relevant incidents) and maintain a Critical Infrastructure Risk Management Program; it may be declared a System of National Significance. - Operators seeking Commonwealth government tenants also need Hosting Certification Framework certification (Certified Assured/Strategic), administered by Home Affairs since 1 May 2023. | NSP与申请人依接入协议商定调试方案，NSP对接入资产进行检验和测试（cl 5.7）。 - 大型逆变器型负荷方面，ERC0394及AEMO过渡指引设想在释放全部负荷前完成模型验证及类似发电机R2测试的扰动穿越测试；通常分5–10年逐步爬坡。 - 投运后，为政府或其他关键基础设施运营者存储/处理业务关键数据的商业数据中心，属Security of Critical Infrastructure Act 2018下的“关键数据存储或处理资产”。 - 责任实体须在成为该类资产后6个月内登入Register of Critical Infrastructure Assets，报告网络安全事件（重大事件12小时、其他相关事件72小时），维持Critical Infrastructure Risk Management Program，并可能被宣布为System of National Significance。 - 拟承接联邦政府租户的运营商还须取得Hosting Certification Framework认证（Certified Assured/Strategic），该框架自2023年5月1日起由Home Affairs管理。 | NSP and AEMO (commissioning); Cyber and Infrastructure Security Centre, Department of Home Affairs (SOCI, Hosting Certification) | NER cl 5.7 (inspection and testing), 5.8 (commissioning), Schedule 5.5; Security of Critical Infrastructure Act 2018 (Cth) Parts 2, 2A, 2B, 2C and s 12F (critical data storage or processing asset); Hosting Certification Framework (Whole-of-Government Hosting Strategy) | Commissioning 2–6 months per stage; SOCI registration within 6 months of operation | NSW, VIC, QLD, WA, SA, TAS, ACT, NT | State electrical safety and technical regulators (e.g. SA Office of the Technical Regulator, WA Building and Energy, Energy Safe Victoria) separately certify installations before energisation; SOCI obligations are Commonwealth-only. | 送电前，各州电气安全及技术监管机构（如SA Office of the Technical Regulator、WA Building and Energy、Energy Safe Victoria）另行认证安装工程；SOCI义务只在联邦层面。 | https://www.cisc.gov.au/information-for-your-industry/data-storage-and-processing/legislation-regulation-and-compliance/soci-act-2018 ¦ https://www.hostingcertification.gov.au/ ¦ https://www.aemc.gov.au/rule-changes/improving-nem-access-standards-package-2
FED | 9 | Emerging national data centre standards: REGO offset, firm capacity, registration and demand flexibility | 全国数据中心标准：REGO、可靠容量与注册 | Following the Prime Minister's 15 July 2026 announcement, the AEMC's 5 August 2026 advice and the National Cabinet decision of 26 August 2026, the Commonwealth intends to legislate (early 2027) mandatory standards for large-scale, hyperscale and AI compute data centres. - Underwrite new supply: REGO certificates from new renewable generation, expected 12 months after endorsement; Queensland and NT secured an 'energy-agnostic' firming approach. - Hold firm capacity contracts, pay full transmission and distribution costs, register with AEMO and provide demand flexibility. - Water efficiency and siting requirements also apply. - These standards 'sit on top of' state planning regimes, so a proponent must satisfy both. - Coverage thresholds and the legislative vehicle (likely the corporations power plus NER changes) are still being consulted on; treat details as provisional. - 17 September 2026: PM&C's consultation paper proposes a tiered scope - under 30 MW excluded, 30-100 MW baseline obligations, above 100 MW or a 150 MW cumulative portfolio substantial obligations; submissions close 9 October 2026. - The Clean Energy Regulator would administer certificate surrender and the AER would review modifications; states keep planning approval powers and may set more stringent requirements, with pipeline projects treated differently by development stage. | 在总理2026年7月15日宣布、AEMC 8月5日建议及国家内阁8月26日决定之后，联邦拟于2027年初立法，对大型、超大规模及AI算力数据中心设定强制标准。 - 承保新增供应：购买并注销新建可再生能源的REGO证书，预计部长认可后12个月生效；昆州和北领地争取到“能源技术中立”的可靠容量方式。 - 持有可靠容量合约、全额承担输配电成本、向AEMO注册并提供需求灵活性。 - 另设用水效率及选址要求。 - 标准“叠加”于州规划制度之上，业主须两头满足。 - 适用门槛及立法载体（可能借助公司权并配合NER修改）仍在咨询，细节应视为暂定。 - 2026年9月17日，PM&C咨询文件提出分级适用：30 MW以下不适用，30–100 MW适用基础义务，100 MW以上或组合容量150 MW以上适用加强义务；意见征集至10月9日。 - 证书注销由Clean Energy Regulator执行，相关调整由AER复核；各州保留规划审批权并可设定更严格要求，在建管线项目按开发阶段区别对待。 | Commonwealth Parliament / DCCEEW; ECMC; AEMC/AEMO for NER implementation | National Cabinet decision 26 Aug 2026 (legislation pending); AEMC advice to ECMC (5 Aug 2026); proposed NER amendments (ERC0448, Package 2, ERC0455); Renewable Electricity Guarantee of Origin scheme (Future Made in Australia (Guarantee of Origin) Act 2024) | Legislation early 2027; REGO obligation ~12 months and registration/connection reforms 24–36 months after endorsement | NSW, VIC, QLD, WA, SA, TAS, ACT, NT | States may impose stricter but not weaker requirements; NSW (Guidelines Aug 2026), ACT (Framework Aug 2026), Tasmania (Draft Expectations Sept 2026) and SA (proposed Act) are already layering their own energy conditions into planning approvals. | 各州可加严但不得放松；新州（2026年8月指引）、首都领地（2026年8月框架）、塔州（2026年9月期望草案）及南澳（拟议法案）已在规划审批中加入各自的能源条件。 | https://www.claytonutz.com/insights/2026/august/nine-governments-one-rulebook-national-cabinet-backs-mandatory-ai-and-data-centre-standards ¦ https://www.abc.net.au/news/2026-08-24/ai-data-centre-energy-rules-override-qld/107068536 ¦ https://www.pv-tech.org/australias-data-centre-energy-rules-take-shape-as-aemc-publishes-framework-and-nsw-moves-to-control-grid-access/
NSW | 1 | Site selection, zoning check and DPHI concierge / Investment Delivery Authority engagement | 选址、分区核查及DPHI/IDA对接 | Data centres are a type of 'high-technology industry' across NSW SEPPs (2021 amendments), permissible with consent in most industrial (E4/E5) and some business zones under the local environmental plan. - The Guidelines encourage siting in productive industrial lands identified in the Sydney Plan and away from residential areas. - DPHI runs a dedicated concierge service and a data centre planning assessment team. - The Investment Delivery Authority (IDA) can endorse major projects: 15 data centres among $51.9 bn endorsed by mid-2026. - Proponents are expected to engage Transgrid/DNSPs, Sydney Water and fibre carriers at this stage; Guidelines Performance Measure 12 asks for early engagement on underground fibre conduits. | 新州各SEPP（2021年修订）把数据中心归入“高技术产业”，在多数工业区（E4/E5）及部分商业区可依地方环境规划经许可开发。 - 指引鼓励选址于Sydney Plan划定的生产性工业用地，远离住宅区。 - DPHI设有专门的礼宾服务及数据中心规划评估团队。 - Investment Delivery Authority（IDA）可为重大项目背书：截至2026年中背书项目519亿澳元，其中数据中心15个。 - 此阶段应着手与Transgrid/DNSP、Sydney Water及光纤运营商接洽；指引绩效指标12要求就地下光纤管道提前沟通。 | Local council LEP zoning; DPHI concierge; Investment Delivery Authority (Premier's Department) | Environmental Planning and Assessment Act 1979 (NSW); Standard Instrument LEP land-use table; SEPP (Industry and Employment) 2021 data centre definition | 2–6 months | FED | FIRB screening and the Commonwealth's data centre expectations run alongside site selection; Transgrid's readiness tests require land ownership or lease to be secured. | FIRB审查及联邦数据中心期望框架与选址同步推进；Transgrid的准备度测试要求已落实土地所有权或租约。 | https://www.planning.nsw.gov.au/policy-and-legislation/planning-reforms/ssd-warehouses-and-data-centres ¦ https://www.infrastructure.nsw.gov.au/media/4jlictae/id0073_nsw-data-centre_guidelines.pdf ¦ https://www.ashurstperkinscoie.com/en/insights/australia-evolving-data-centre-landscape-policy-meets-pipeline/
NSW | 2 | State Significant Development consent: SEARs, EIS, exhibition and determination | SSD许可：SEARs、EIS、公示与裁定 | A data centre with electrical capacity above 15 MW is SSD under s 4.36 of the EP&A Act and Schedule 1 of the SEPP (Planning Systems) 2021; smaller facilities over $30 m CIV are regionally significant and go to a planning panel. - The proponent requests Secretary's Environmental Assessment Requirements (Guidelines commit to SEARs within two months). - The EIS must address the Guidelines' performance measures: PUE ≤1.25, WUE limits, 100% recycled water for cooling or a committed transition, drought resilience, 25% demand reduction for 2 hours without diesel, PPA commitments from year 4, no diesel for load-shifting. - DPHI exhibits the EIS, seeks agency advice (EPA, Transgrid/DNSP, Sydney Water, TfNSW) and assesses within a 75-day target 'in government hands'. - The Minister/delegate determines, or the IPC where there are more than 50 objections or a reportable political donation. - Conditions of consent increasingly lock in energy commitments and annual compliance reporting. | 电力容量超过15 MW的数据中心依EP&A Act s 4.36及SEPP (Planning Systems) 2021 Schedule 1属SSD；CIV超过3000万澳元但未达该门槛的项目属区域重大开发，交规划委员会裁定。 - 业主申请SEARs，指引承诺两个月内出具。 - EIS须逐项回应指引绩效指标：PUE≤1.25、WUE上限、冷却100%使用再生水或承诺过渡、抗旱能力、不靠柴油实现2小时削减25%需求、第4年起PPA承诺、不得用柴油转移负荷。 - DPHI公示EIS、征求EPA、Transgrid/DNSP、Sydney Water、TfNSW意见，并在“政府手中”75天目标内完成评估。 - 由部长/受权人裁定；反对意见超过50份或涉及须申报政治捐款的，交IPC裁定。 - 许可条件正日益把能源承诺及年度合规报告固化为约束。 | DPHI (assessment); Minister for Planning or delegate / Independent Planning Commission (determination) | EP&A Act 1979 s 4.36, Div 4.7; SEPP (Planning Systems) 2021 Sch 1 (data centres >15 MW); EP&A Regulation 2021; NSW Data Centre Guidelines (Aug 2026, non-statutory but applied through SEARs and conditions) | SEARs ~2 months; EIS preparation 6–12 months; assessment 75-day target (historically 9–18 months) | FED | EPBC referral, if triggered, is coordinated under the NSW–Commonwealth bilateral assessment agreement; the NER connection process runs concurrently and Transgrid/DNSP capacity advice is a referral input to the SSD assessment. | 如触发EPBC转介，依新州–联邦双边评估协议协调办理；NER接入程序同步推进，Transgrid/DNSP的容量意见作为转介意见纳入SSD评估。 | https://www.gadens.com/insights/data-centre-planning-approvals-in-new-south-wales-powering-the-future,-planning-for-the-present ¦ https://www.infrastructure.nsw.gov.au/media/4jlictae/id0073_nsw-data-centre_guidelines.pdf ¦ https://www.claytonutz.com/insights/2026/august/nsw-draws-the-line-what-the-new-data-centre-policy-framework-means-for-investors-developers-government-and-communities
NSW | 3 | Environmental licensing and water servicing agreements | 环境许可与供水服务协议 | Large standby generator fleets (diesel or gas) can exceed the electricity generation threshold in Schedule 1 of the Protection of the Environment Operations Act 1997 (30 MW for fossil-fuel generation) and then need an Environment Protection Licence from the NSW EPA. - The EPA also regulates noise and air emissions through consent conditions; the Guidelines discourage diesel for anything but emergency backup. - Water: Performance Measures 2, 3 and 11 require recycled or rainfall-independent water for cooling. - A Sydney Water/Hunter Water servicing agreement is required, with the proponent funding 100% of pipeline augmentation and possibly accepting take-or-pay terms; IPART has been asked to review a data-centre water pricing framework. - These are conditions precedent to occupation rather than to grid connection, but network operators increasingly ask to see them. | 大型备用机组（柴油或燃气）可能超过Protection of the Environment Operations Act 1997 Schedule 1的发电门槛（化石燃料发电30 MW），需向NSW EPA申领Environment Protection Licence。 - EPA还通过许可条件管控噪声及空气排放；指引不鼓励柴油机用于应急备用以外的用途。 - 用水：绩效指标2、3、11要求冷却使用再生水或不依赖降雨的水源。 - 须与Sydney Water/Hunter Water签订服务协议，业主承担100%管网增容费用，并可能接受照付不议条款；IPART已受命审查数据中心水价框架。 - 上述均为入驻而非并网的前置条件，但网络运营商越来越多地要求查验。 | NSW EPA; Sydney Water / Hunter Water; IPART | Protection of the Environment Operations Act 1997 (NSW) Sch 1 (electricity generation) and Ch 3 (licensing); Sydney Water Act 1994 s 73 servicing; NSW Data Centre Guidelines PM 2, 3, 11 | 3–9 months, in parallel with SSD assessment | FED | National Cabinet's water-efficiency and 'fund additional water infrastructure' standard will overlay the NSW water performance measures once legislated. | 国家内阁的用水效率及“出资建设额外供水基础设施”标准立法后，将叠加于新州的用水绩效指标之上。 | https://www.infrastructure.nsw.gov.au/media/4jlictae/id0073_nsw-data-centre_guidelines.pdf ¦ https://www.pinsentmasons.com/out-law/analysis/australia-new-data-centre-rules-mean-planning-environment
NSW | 4 | Connection enquiry and capacity assessment with Transgrid or the DNSP; Transgrid Network Capacity Allocation Policy | 接入咨询与Transgrid容量分配政策 | Loads up to roughly 30–60 MW usually connect to Ausgrid, Endeavour Energy or Essential Energy at 11–132 kV under NER Chapter 5A (negotiated connection) or Chapter 5; larger campuses connect directly to Transgrid's 132/330 kV network under Chapter 5. - The NER enquiry/response steps (cl 5.3.2–5.3.3) apply. - Transgrid's Network Capacity Allocation Policy (effective 14 August 2026, inverter-based loads ≥30 MW/MVA) allocates capacity only on signature of a Network Connection Agreement, and offers a 'conditional NCA' before performance standards are finalised. - Five readiness criteria must be met within three months: planning approval matching the requested capacity plus FIRB where needed; construction contracts or underwriting; land secured; long-lead equipment contracts; financing/board approval. Otherwise the NCA terminates and capacity is lost. - Transgrid reports more than 10 GW of data centre enquiries statewide and says Sydney-basin transmission capacity is largely exhausted. - It publishes quarterly capacity updates and is developing a 25-year data centre forecast with the DNSPs. | 约30–60 MW以下负荷通常依NER第5A章（协商接入）或第5章，以11–132 kV接入Ausgrid、Endeavour Energy或Essential Energy；更大园区依第5章直接接入Transgrid的132/330 kV网络。 - NER咨询/回复步骤（cl 5.3.2–5.3.3）照常适用。 - Transgrid的Network Capacity Allocation Policy（2026年8月14日生效，适用于30 MW/MVA及以上逆变器型负荷）规定仅在签署Network Connection Agreement后分配容量，性能标准定稿前可先签“有条件NCA”。 - 三个月内须满足五项准备度标准：与申请容量匹配的规划批准（必要时含FIRB）、施工合同或承保、土地落实、长周期设备合同、融资/董事会批准；否则NCA终止、容量收回。 - Transgrid称全州数据中心咨询已超10 GW，悉尼盆地输电容量基本耗尽。 - Transgrid每季发布容量更新，并与DNSP联合编制25年数据中心负荷预测。 | Transgrid (TNSP) or Ausgrid / Endeavour Energy / Essential Energy (DNSP) | NER cl 5.3.2–5.3.3 and Chapter 5A Part D (negotiated distribution connections); Transgrid Network Capacity Allocation Policy (Aug 2026, contractual policy, not a rule) | Enquiry response 30–40 business days; capacity allocation only on NCA signature | FED | The NER Chapter 5 process is the legal backbone; Transgrid's policy and the pending state access scheme add state-specific gating on top of it. | NER第5章程序是法律主干，Transgrid政策及待出台的州接入计划在其上叠加了新州特有的门槛。 | https://www.transgrid.com.au/about-us/network/network-connections/data-centres-and-electricity-capacity-in-nsw/ ¦ https://w.media/transgrid-sets-six-tests-for-data-centres-seeking-nsw-grid-capacity/ ¦ https://www.transgrid.com.au/media/c0hbf1gj/20260617-update-on-network-capacity.pdf
NSW | 5 | Application to connect, performance standards and connection offer/agreement | 接入申请、性能标准与接入报价/协议 | The applicant lodges the NER cl 5.3.4 application with models and proposed access standards; Transgrid and AEMO assess negotiated standards (cl 5.3.4A) and, for ≥30 MW inverter-based loads, the ride-through and instability-detection standards being finalised under ERC0394. - Transgrid's sixth readiness test is a complete performance-standards package accepted by AEMO and Transgrid. - The offer to connect (cl 5.3.6, four-month statutory target) leads to a Network Connection Agreement covering connection assets (user-funded), any shared-network augmentation, security and demand profile. - The NSW consultation paper (August 2026) proposes that connection agreements for ≥15 MW data centres include binding annual demand profiles with exceedance penalties and a 'negative ratchet'. - It also proposes quarterly information provision to NSPs/AER/AEMO/EnergyCo, enforcement of PPA/firming commitments, and a demand-management obligation to cut load 25% for up to two hours on NSP or AEMO signal. | 申请人依NER cl 5.3.4提交申请，附模型及拟议接入标准；Transgrid与AEMO评估协商标准（cl 5.3.4A），30 MW及以上逆变器型负荷还需满足ERC0394正在定稿的穿越及失稳检测标准。 - Transgrid第六项准备度测试，就是经AEMO和Transgrid接受的完整性能标准包。 - 接入报价（cl 5.3.6，法定目标4个月）后签署Network Connection Agreement，涵盖接入资产（用户出资）、共享网络增容、担保及需求曲线。 - 新州2026年8月咨询文件建议：15 MW及以上数据中心的接入协议纳入约束性年度需求曲线，超额受罚并设“负向棘轮”。 - 另建议：每季向NSP/AER/AEMO/EnergyCo报送信息、强制执行PPA/可靠容量承诺、按NSP或AEMO信号在最长两小时内削减25%负荷。 | Transgrid / DNSP; AEMO (advisory matters) | NER cl 5.3.4, 5.3.4A, 5.3.5–5.3.7; Schedule 5.3; proposed Electricity Infrastructure Investment Regulation amendments (Q4 2026) | 6–18 months from application to executed agreement | FED | Identical NER clauses apply nationally; NSW proposes to derogate from the NER via the EII Act to add state-specific contractual terms. | NER相关条款全国统一；新州拟借EII Act偏离NER，加入州特有的合同条款。 | https://www.mallesons.com/au/en/insights/latest-thinking/another-big-day-for-data-centres-in-nsw-a-new-framework-for-connection.html ¦ https://www.aemc.gov.au/rule-changes/improving-nem-access-standards-package-2
NSW | 6 | Network augmentation, cost allocation and NSW-specific fees (entry bond, Major Network Upgrade Fee, take-or-pay) | 增容成本分担及新州特有费用 | Under the NER, dedicated connection assets are paid by the applicant while shared augmentation passing the RIT-T/RIT-D is socialised, an outcome NSW considers unacceptable for data centres. - The August 2026 consultation paper (submissions closed 14 September 2026) proposes for ≥15 MW data centres a $30,000/MW entry bond at application, held by the Scheme Financial Vehicle. - A Major Network Upgrade Fee of $200,000/MW in the Sydney–Newcastle–Wollongong area or $100,000/MW elsewhere, payable before NCA execution and set by the Consumer Trustee. - Guaranteed minimum use-of-system charges (take-or-pay, potentially 10 years); DNSP recovery of Transgrid augmentation costs from distribution-connected data centres; contributions by transmission-connected data centres to the Electricity Infrastructure Fund and Climate Change Fund. - The Bill also broadens the 'network operator' definition and bars the Consumer Trustee from maximising access fees. - Regulations are targeted for Q4 2026; treat figures as proposals until made. | 按NER，专用接入资产由申请人付费，通过RIT-T/RIT-D的共享增容则由全体用户分摊——新州认为这对数据中心不可接受。 - 2026年8月咨询文件（意见征集于9月14日截止）对15 MW及以上数据中心提出：申请时缴纳每MW 3万澳元入门保证金，由Scheme Financial Vehicle托管。 - Major Network Upgrade Fee：悉尼–纽卡斯尔–卧龙岗地区每MW 20万澳元，其他地区每MW 10万澳元，签署NCA前缴纳，金额由Consumer Trustee设定。 - 保证最低网络使用费（照付不议，可能长达10年）；DNSP向配网接入的数据中心回收Transgrid增容成本；输电接入的数据中心向Electricity Infrastructure Fund及Climate Change Fund缴款。 - 法案同时扩大“network operator”定义，并禁止Consumer Trustee以接入费最大化为目标。 - 法规拟2026年四季度出台；正式颁布前上述数字均为提案。 | NSW Minister for Energy / EnergyCo; Consumer Trustee (AEMO Services); Scheme Financial Vehicle; NSPs; AER for NER elements | Electricity Infrastructure Investment Act 2020 (NSW) as amended by the Electricity Infrastructure Investment Amendment Bill 2026 (introduced 5 Aug 2026); proposed regulations Q4 2026; NER cl 5.16/5.17, Chapter 6A Part D | Fees payable at application and pre-NCA; regulations expected Q4 2026 | FED | The federal cost-recovery rule changes (ERC0448/Package 2) pursue the same objective nationally; NSW is moving first via state law and derogation from the NER. | 联邦成本回收规则修改（ERC0448/第二批）在全国层面追求同一目标；新州则通过州法和偏离NER先行一步。 | https://www.mallesons.com/au/en/insights/latest-thinking/another-big-day-for-data-centres-in-nsw-a-new-framework-for-connection.html ¦ https://www.energy.nsw.gov.au/nsw-plans-and-progress/regulation-and-policy/public-consultations/data-centres ¦ https://legislation.nsw.gov.au/view/pdf/bill/affe6b31-bef0-49e6-98e1-f9eac558401a
NSW | 7 | Large load access scheme (competitive allocation of grid access) | 大负荷接入计划：电网接入竞争性分配 | The Amendment Bill lets the Minister declare a 'large load access scheme' for infrastructure capable of transmitting 5 MW or more (or a higher prescribed threshold), modelled on Renewable Energy Zone access schemes. - Access rights in constrained parts of the network would be allocated competitively (tender rather than first-come-first-served) against merit criteria such as energy and water efficiency, demand flexibility and financial capacity. - Capacity limits would be set by system capability, with future rounds tied to projects such as the Hunter Transmission Project; access rights would be conditional and enforceable. - The second reading speech confirms the intent is to manage data centres rather than hospitals or rail. - Consultation on scheme design is flagged from late 2026 into the first half of 2027; no scheme is yet in force. - The Bill passed the Legislative Assembly on 15 September 2026 and is before the Legislative Council; the declaration power is not yet law and no large load access scheme has been declared. | 修正法案授权部长对输送能力5 MW及以上（或法规规定的更高门槛）的设施宣布“大负荷接入计划”，模式参照Renewable Energy Zone接入计划。 - 受限网络区域的接入权改为竞争性分配（招标而非先到先得），评分标准包括能源与用水效率、需求灵活性及财务实力。 - 容量上限按系统能力设定，后续轮次与Hunter Transmission Project等工程挂钩；接入权附条件并可强制执行。 - 二读发言明确，政策目标是管理数据中心，而非医院或铁路。 - 计划设计咨询拟于2026年底至2027年上半年进行，目前尚无计划生效。 - 法案于2026年9月15日通过众议院，现待上议院审议；宣布权尚未生效，目前未宣布任何大负荷接入计划。 | NSW Minister for Energy; EnergyCo; Consumer Trustee | Electricity Infrastructure Investment Amendment Bill 2026 (NSW) – new large load access scheme provisions (Bill before Parliament as of Sept 2026) | Scheme design consultation late 2026 – H1 2027; first allocations unlikely before 2027–28 | FED | An access scheme would override the NER's open-access presumption for the declared area, which is why the Bill includes power to derogate from the NER; AEMO Services acts as Consumer Trustee under NSW law. | 接入计划将在宣布区域内取代NER的开放接入推定，因此法案纳入了偏离NER的授权；AEMO Services依新州法律担任Consumer Trustee。 | https://www.pv-tech.org/australias-data-centre-energy-rules-take-shape-as-aemc-publishes-framework-and-nsw-moves-to-control-grid-access/ ¦ https://www.mallesons.com/au/en/insights/latest-thinking/another-big-day-for-data-centres-in-nsw-a-new-framework-for-connection.html
NSW | 8 | Retailer/PPA, firming and AEMO registration decisions | 零售商/PPA、可靠容量与AEMO注册 | A retailer must be appointed as FRMP before energisation; the data centre may also register directly with AEMO as a Market Customer. - The NSW Guidelines (PM 13–14) require, from year four of operation, contracted renewable energy equal to annual average demand under PPAs of at least 10 years with projects not yet at financial investment decision. - At least 40% wind by MWh, and storage of at least 25% of contracted generation capacity for four hours. - The proposed connection regulations would let NSPs enforce these commitments by reducing allocated capacity. - The forthcoming national REGO and firm-capacity obligations and AEMO registration for large facilities would sit alongside these state requirements. | 送电前须指定零售商为FRMP；数据中心亦可直接向AEMO注册为Market Customer。 - 新州指引（PM 13–14）要求自运营第4年起，合同可再生能源电量与年均需求相当，PPA期限至少10年，对手方项目须尚未作出最终投资决定。 - 按MWh计风电占比至少40%，并配套不低于合同发电容量25%、时长4小时的储能。 - 拟议接入法规允许NSP以削减已分配容量的方式强制执行上述承诺。 - 即将出台的全国REGO、可靠容量义务及大型设施AEMO注册要求，将与这些州级要求并行。 | Retailer (FRMP); AEMO; DPHI via consent conditions; NSPs via connection agreements | NER Chapter 2 (registration); NSW Data Centre Guidelines PM 13–14; proposed EII regulations (PPA/firming enforcement) | PPA procurement 6–18 months; obligations bite from year 4 of operation | FED | NSW's PPA metrics are stricter and earlier than the national REGO scheme; the Commonwealth has said states may go further but not weaker. | 新州的PPA指标比全国REGO机制更严、更早生效；联邦已表明各州可加严但不得放松。 | https://www.infrastructure.nsw.gov.au/media/4jlictae/id0073_nsw-data-centre_guidelines.pdf ¦ https://www.aemc.gov.au/news-centre/media-releases/data-centres-bring-clean-firm-energy-be-flexible-and-pay-their-way-aemc-advises-ministers
NSW | 9 | Construction certificates, metering, commissioning and energisation | 施工许可、计量、调试与送电 | After SSD consent the proponent obtains construction certificates from a registered certifier under Part 6 of the EP&A Act. - Transmission connection works are either built by the proponent as contestable works or by Transgrid/DNSP. - Metering (NER Chapter 7) and a nominated FRMP are prerequisites to energisation; the NSP witnesses commissioning and the connection is typically energised in stages tied to consented capacity. - Transgrid's policy converts provisional capacity to permanent only when readiness criteria are met. - Post-energisation, the proposed regulations would require ongoing demand-profile compliance reporting and the Guidelines contemplate annual audits. | 取得SSD许可后，业主依EP&A Act Part 6由注册审核员签发施工许可证。 - 输电接入工程可作为可竞争工程自建，或委托Transgrid/DNSP建设。 - 计量（NER第7章）及指定FRMP是送电前提；NSP见证调试，接入通常按获批容量分阶段送电。 - Transgrid政策下，临时容量须待准备度标准满足后才转为永久容量。 - 送电后，拟议法规要求持续报送需求曲线合规情况，指引亦设有年度审计。 | Registered certifier / DPHI (construction & occupation certificates); Transgrid / DNSP (commissioning); AEMO (metering systems) | EP&A Act 1979 Part 6 (certification); NER cl 5.7–5.8, Chapter 7 | Construction 18–30 months; commissioning 2–6 months per stage | FED | Commissioning tests follow national NER/AEMO procedures; NSW adds occupation certificate and consent-condition compliance as gating items. | 调试测试遵循全国NER/AEMO程序；新州另把入驻证书及许可条件合规列为门槛事项。 | https://www.transgrid.com.au/about-us/network/network-connections/data-centres-and-electricity-capacity-in-nsw/ ¦ https://www.infrastructure.nsw.gov.au/media/4jlictae/id0073_nsw-data-centre_guidelines.pdf
VIC | 1 | Site selection, zoning and Industrial Land Gateway / Invest Victoria facilitation | 选址、分区及Invest Victoria协调 | The VPP has no stand-alone 'data centre' land-use term; the use is generally characterised as a utility installation or warehouse-type industry (Tract notes VC159 left it without a formal definition). - Permissibility therefore depends on the zone table: Industrial 1 and 3 Zones and Commercial 2 Zone are the usual homes, sometimes Mixed Use. - Where rezoning is needed, the State's Industrial Land Gateway Service and the 10-year Plan for Industrial Land prioritise digital infrastructure sites. - Invest Victoria and the Investment Coordinator-General (appointed early 2025) provide a concierge role. - Proponents should also check Melbourne Water recycled water availability and cultural heritage (Aboriginal Heritage Act 2006 CHMP triggers) at this stage. - The Sustainable Data Centre Action Plan (22 September 2026) will insert a stand-alone 'data centre' land-use term - land used to collect, distribute, process or store digital data - prohibit the use in residential and Green Wedge zones, and allow rural zones only near transmission, substations, renewables, storage or recycled water infrastructure. | VPP没有独立的“data centre”用途类别，通常归为utility installation或仓储型工业（Tract指出VC159未给出正式定义）。 - 可否开发因此取决于分区用途表：常见于Industrial 1区、3区及Commercial 2区，偶见于Mixed Use区。 - 如需重新分区，州Industrial Land Gateway Service及10-year Plan for Industrial Land对数字基础设施场址给予优先。 - Invest Victoria及Investment Coordinator-General（2025年初设立）提供礼宾式协调。 - 此阶段还应核查Melbourne Water再生水供应及文化遗产问题（Aboriginal Heritage Act 2006下的CHMP触发条件）。 - Sustainable Data Centre Action Plan（2026年9月22日）将设立独立的"data centre"用途术语（用于收集、传输、处理或存储数字数据的土地），住宅区及Green Wedge Zone禁止，乡村区仅在靠近输电线路、变电站、可再生电源、储能或再生水设施时方可开发。 | Local council (planning scheme); DTP Industrial Land Gateway; Invest Victoria | Planning and Environment Act 1987 (Vic); Victoria Planning Provisions (zone tables; Amendment VC159 2019); Aboriginal Heritage Act 2006 | 2–6 months (12+ months if rezoning) | FED | FIRB and the Commonwealth data centre expectations apply concurrently; EPBC referral is rare on brownfield industrial land in Melbourne's west and north. | FIRB及联邦数据中心期望框架同步适用；墨尔本西部和北部的棕地工业用地很少触发EPBC转介。 | https://tract.com.au/data-centres-a-planning-perspective/ ¦ https://www.ashurstperkinscoie.com/en/insights/australia-evolving-data-centre-landscape-policy-meets-pipeline/ ¦ https://www.invest.vic.gov.au/explore-your-sector/digital-technology/data-centres
VIC | 2 | Planning permit: council pathway or Development Facilitation Program (clause 53.22) ministerial permit | 规划许可：议会路径或DFP部长许可 | A standard planning permit application goes to the council as responsible authority under s 47 of the P&E Act, with public notice (s 52) and third-party review rights at VCAT; determination typically takes 6–12 months for large industrial buildings. - Alternatively, projects meeting the Development Facilitation Program criteria (a significant economic development above a stated investment threshold; Ashurst cites $20 m+ development cost, though published thresholds have varied and should be confirmed with DTP) can be declared eligible. - The Minister for Planning then becomes responsible authority under clause 53.22; no notice or third-party appeal applies, and DTP targets a decision within about four months. - Multiple hyperscale campuses in Melbourne's north and west have used this route (ministerial permits PA2403014, PA2504019, PA2604506 etc.). - An Environment Effects Statement under the Environment Effects Act 1978 is only required if the Minister decides the project may have significant environmental effects, which has not been typical for data centres. - Under the Action Plan a 150 m buffer from residential buildings applies, design WUE must be 1.0 or better on potable water and 1.6 on non-potable (ISO/IEC 30134-9:2022), the Minister for Planning stays responsible authority only for Development Facilitation Program applications, and the new controls do not apply retrospectively to applications already under assessment. | 标准路径下，规划许可申请依P&E Act s 47向作为责任机构的地方议会提交，须公告（s 52），第三方可向VCAT申请复审；大型工业建筑通常6–12个月裁定。 - 另一路径是Development Facilitation Program：符合重大经济开发及投资门槛的项目可被宣布合格（Ashurst引述开发成本2000万澳元以上，但公布门槛曾有变动，应向DTP确认）。 - 此后规划部长依clause 53.22成为责任机构，无需公告、无第三方上诉，DTP目标约四个月内决定。 - 墨尔本北部和西部多个超大规模园区已走此路径（部长许可PA2403014、PA2504019、PA2604506等）。 - 仅当部长认定项目可能产生重大环境影响时，才需依Environment Effects Act 1978编制EES，数据中心项目一般不涉及。 - 行动计划要求与住宅建筑保持150米退让；设计WUE不高于1.0（自来水）或1.6（非饮用水，按ISO/IEC 30134-9:2022）；规划部长仅对开发促进计划项目继续作为责任机构；新控制不溯及已在审申请。 | Local council or Minister for Planning (DFP / clause 53.22); VCAT for reviews (council pathway only) | Planning and Environment Act 1987 ss 47–64 (permits), s 20(4) exemptions; VPP clause 53.22 Significant Economic Development; Environment Effects Act 1978 | Council 6–12 months; DFP ~4 months from acceptance | FED | Where EPBC applies, Victoria's bilateral agreement allows the EES/permit process to serve as the Commonwealth assessment; National Cabinet's siting standards will overlay planning decisions once legislated. | 如适用EPBC，维州双边协议允许以EES/许可程序充当联邦评估；国家内阁选址标准立法后将叠加于规划决定。 | https://tract.com.au/data-centres-a-planning-perspective/ ¦ https://www.planning.vic.gov.au/planning-approvals/ministerial-permits-register/ministerial-permits/76685df6-baaf-f011-bbd2-6045bdc32df2 ¦ https://www.ashurstperkinscoie.com/en/insights/australia-evolving-data-centre-landscape-policy-meets-pipeline/
VIC | 3 | Environmental approvals: EPA Victoria permissions and Energy Safe Victoria | EPA Victoria许可与电气安全签核 | Under the Environment Protection Act 2017 the general environmental duty applies to construction and operation. - A development licence/operating licence or registration from EPA Victoria is needed only if site activities fall within the prescribed permission activities in the Environment Protection Regulations 2021. - Large fossil-fuel generation and fuel storage thresholds can capture big diesel backup fleets and bulk diesel tanks. - Noise is regulated through the Noise Protocol referenced in the Regulations and in permit conditions. - Energy Safe Victoria oversees electrical installation safety and must be satisfied under the Electricity Safety Act 1998 before large installations are energised. | 依Environment Protection Act 2017，一般环境义务贯穿建设与运营全程。 - 仅当场址活动落入Environment Protection Regulations 2021规定的许可活动时，才需向EPA Victoria申领开发许可/运营许可或办理登记。 - 大型化石燃料发电及燃油储存门槛可能覆盖大规模柴油备用机组和大型柴油储罐。 - 噪声按条例引用的Noise Protocol及许可条件管控。 - Energy Safe Victoria监管电气安装安全，大型装置送电前须依Electricity Safety Act 1998获其认可。 | EPA Victoria; Energy Safe Victoria | Environment Protection Act 2017 (Vic) Part 3.2 general environmental duty, Part 4 permissions; Environment Protection Regulations 2021 Sch 1; Electricity Safety Act 1998 | 3–6 months, in parallel with permit | FED | No Commonwealth equivalent unless EPBC is triggered; SOCI obligations are separate and federal. | 除触发EPBC外没有联邦对应程序；SOCI义务是独立的联邦事项。 | https://tract.com.au/data-centres-a-planning-perspective/
VIC | 4 | Transmission connection via VicGrid (pre-feasibility, enquiry, application) with AusNet as DTSO | VicGrid输电接入六阶段流程 | Since VicGrid took over Victoria's transmission planning and connection functions from AEMO (National Electricity (Victoria) Act 2005 amendments), a transmission-connected load lodges its NER cl 5.3.2 enquiry through VicGrid's six-stage process. - Stages: 1 pre-feasibility (optional), 2 enquiry, 3A pre-application, 3 application, 4 contracts, 5 construction, 6 completion. - AusNet Transmission (DTSO/TNSP for the Declared Shared Network) builds and owns the connection to its terminal stations. - AusNet reports it connected Australia's first transmission-level data centre in 2024 and offers due-diligence, connection-equipment and fibre services. - Community Engagement and Social Value Guidelines now apply to applicants; a new Victorian Access Regime is due in 2027 with transitional arrangements in the interim. - VicGrid's published material is renewables-oriented and load-specific guidance is limited. - From the Action Plan (22 September 2026) VicGrid becomes a statutory referral authority for every data centre planning application, including council-determined ones, assessing grid impact before a permit issues. | VicGrid依National Electricity (Victoria) Act 2005修正案从AEMO接手维州输电规划及接入职能后，输电接入负荷通过VicGrid六阶段流程提交NER cl 5.3.2咨询。 - 六阶段为：1 预可行性（可选）、2 咨询、3A 预申请、3 申请、4 合同、5 建设、6 完成。 - AusNet Transmission（Declared Shared Network的DTSO/TNSP）建设并持有至其终端站的接入设施。 - AusNet称2024年已接入全澳首个输电级数据中心，并提供尽调、接入设备及光纤服务。 - Community Engagement and Social Value Guidelines现已适用于申请人；新的Victorian Access Regime拟2027年实施，过渡期适用临时安排。 - VicGrid公开材料以可再生能源为导向，针对负荷侧的指引有限。 - 依行动计划（2026年9月22日），VicGrid成为所有数据中心规划申请的法定转介机构（含议会审批项目），在发证前评估电网影响。 | VicGrid (connection process manager); AusNet Transmission (DTSO/TNSP); AEMO (advisory matters) | NER cl 5.3.2–5.3.4A as modified for Victoria by the National Electricity (Victoria) Act 2005 and NER Chapter 5 Victorian derogations; VicGrid Transmission Connections Process | Enquiry response 30–40 business days; application to offer 12–18 months for large loads | FED | The NER Chapter 5 clauses apply but with Victoria-specific derogations giving VicGrid (not the TNSP) the planning role; AEMO retains advisory-matter approvals. | NER第5章条款照常适用，但维州特有的偏离条款把规划职能交给VicGrid而非TNSP；AEMO保留对咨询事项的批准权。 | https://www.vicgrid.com.au/industry/access-and-connections/transmission-connections-process ¦ https://www.ausnetservices.com.au/projects-and-innovation/data-centres ¦ https://www.vicgrid.com.au/__data/assets/pdf_file/0045/768996/guidelines-for-establishing-connection-to-DSN-terminal-stations.pdf
VIC | 5 | Distribution connection with AusNet / CitiPower-Powercor / Jemena / United Energy (NER Chapter 5A / 5) | 维州五家DNSP配电接入（NER第5A/5章） | Loads in the 10–60 MW range often connect at 22 kV or 66 kV to one of Victoria's five DNSPs: Jemena and CitiPower (inner north and CBD), Powercor (west), United Energy (south-east) and AusNet (east/north-east). - The DNSP processes enquiry and application under NER Chapter 5A Part D (negotiated connection, offer due within 65 business days of a complete application) or Chapter 5 for the largest sites. - Its AER-approved connection policy governs capital contributions: connection assets and zone-substation augmentation attributable to the load are generally customer-funded. - The ESC's Electricity Distribution Code of Practice governs supply standards, and 66 kV sub-transmission augmentation may itself require a RIT-D. - Capacity in the western and northern growth corridors is contested by multiple campuses, so early enquiry and staged capacity requests are essential. | 10–60 MW负荷通常以22 kV或66 kV接入维州五家DNSP之一：Jemena和CitiPower（内北区及CBD）、Powercor（西部）、United Energy（东南部）、AusNet（东部/东北部）。 - DNSP依NER第5A章Part D（协商接入，完整申请后65个工作日内出具报价）处理咨询与申请；最大型场址则走第5章。 - 资本分摊按AER批准的接入政策执行：可归因于该负荷的接入资产及区域变电站增容一般由客户出资。 - ESC的Electricity Distribution Code of Practice规范供电标准；66 kV次输电增容本身可能需要RIT-D。 - 西部和北部增长走廊的容量被多个园区争抢，尽早咨询、分期申请容量是关键。 | DNSP (AusNet, CitiPower/Powercor, Jemena, United Energy); AER (connection policies); ESC | NER Chapter 5A Parts B–E (negotiated connections, connection charges) or Chapter 5; DNSP Connection Policies approved by AER (2026–31 determinations); ESC Electricity Distribution Code of Practice | Offer 65 business days after complete application; total 9–18 months | FED | Pure NER process; Victoria adds ESC code obligations but no data-centre-specific overlay yet. | 纯NER程序；维州叠加了ESC守则义务，但尚无针对数据中心的专门规则。 | https://www.aemc.gov.au/sites/default/files/content/NER-v73-Chapter-05A.PDF ¦ https://www.energex.com.au/__data/assets/pdf_file/0011/1090649/Large-Customer-Connection-Manual-3040635.pdf
VIC | 6 | Connection offer, agreement and augmentation cost allocation | 接入报价、协议与增容成本分担 | The NER cl 5.3.6 offer to connect and cl 5.3.7 connection agreement apply. - For transmission, VicGrid prepares the offer at Stage 4 and AusNet contracts for the connection assets, which the applicant funds as negotiated transmission services (or builds contestably). - Shared-network augmentation is planned by VicGrid through the Victorian Transmission Plan and, if regulated, must pass the RIT-T (cl 5.16) with costs recovered from all Victorian customers. - That socialised outcome is precisely what the Commonwealth's pending cost-recovery rule changes (ERC0448/Package 2) and National Cabinet's 'pay full transmission and distribution costs' standard aim to reverse. - Unlike NSW, Victoria has not yet announced state-specific bonds, upgrade fees or take-or-pay terms for data centres. - The Action Plan applies a causer-pays expectation through planning: operators fund their own connection and all network augmentation, including upstream upgrades, though Victoria still has no state bond, upgrade fee or take-or-pay term. | NER cl 5.3.6接入报价及cl 5.3.7接入协议照常适用。 - 输电层面由VicGrid在第4阶段出具报价，AusNet就接入资产签约；申请人以协商输电服务方式出资，或以可竞争方式自建。 - 共享网络增容由VicGrid通过Victorian Transmission Plan统筹，属受监管投资的须通过RIT-T（cl 5.16），成本由全体维州用户分摊。 - 这种社会化分摊正是联邦待审成本回收规则修改（ERC0448/第二批）及国家内阁“全额支付输配电成本”标准要扭转的局面。 - 与新州不同，维州尚未针对数据中心宣布州级保证金、升级费或照付不议条款。 - 行动计划通过规划环节确立谁引起谁付费：运营商自行承担接入及全部网络扩建费用，含上游升级；维州仍未设立州级保证金、升级费或照付不议条款。 | VicGrid / AusNet (transmission); DNSPs; AER (RIT-T/RIT-D, revenue determinations) | NER cl 5.3.6–5.3.7, cl 5.16 RIT-T, Chapter 6A Part D; Victorian Transmission Plan (VicGrid, National Electricity (Victoria) Act 2005 Part 3) | Offer 4 months statutory; 6–12 months to executed agreements | FED | Cost allocation is national (NER/AER) with Victorian planning derogations; federal rule changes pending in 2026–27 would shift augmentation costs to data centres nationally. | 成本分担属全国（NER/AER）事项，附维州规划偏离条款；2026–27年待审的联邦规则修改将在全国把增容成本转由数据中心承担。 | https://www.vicgrid.com.au/industry/access-and-connections/transmission-connections-process ¦ https://www.aemc.gov.au/rule-changes/cost-recovery-network-augmentations-package-1
VIC | 7 | Retailer, AEMO registration and metering | 零售商、AEMO注册与计量 | A retailer (FRMP) is appointed or the operator registers with AEMO as a Market Customer. - Victoria imposes no additional state licence on a customer buying electricity, though retailers need an ESC licence. - Metering follows NER Chapter 7 (type 1–4 installations, contestable Metering Coordinator). - The forthcoming national registration and REGO/firm-capacity obligations will apply to Victorian data centres as elsewhere. - Victoria has not announced a state PPA rule, but the Sustainable Data Centre Action Plan flags energy innovation and grid readiness as focus areas. - Action Plan energy actions E1-E5 require new data centres to offset operational electricity with investment in new renewable generation and storage, participate in demand flexibility to the maximum feasible extent and meet best-practice PUE targets, consistent with Victoria's 65% by 2030 and 95% by 2035 renewable targets. | 指定零售商作为FRMP，或由运营商向AEMO注册为Market Customer。 - 维州不对购电客户另设州级许可，但零售商须持ESC牌照。 - 计量遵循NER第7章：1–4类计量装置，Metering Coordinator可竞争选择。 - 即将出台的全国注册及REGO/可靠容量义务对维州数据中心同样适用。 - 维州未宣布州级PPA规则，但Sustainable Data Centre Action Plan将能源创新及电网准备度列为重点。 - 行动计划能源条款E1–E5要求新建数据中心以投资新增可再生发电及储能抵消运营用电、在可行范围内最大程度参与需求灵活性服务，并达到行业最佳实践PUE水平，与维州2030年65%、2035年95%可再生目标衔接。 | Retailer/FRMP; AEMO; ESC (retail licensing) | NER Chapter 2 and Chapter 7; Electricity Industry Act 2000 (Vic) retail licensing | 3–9 months for retail/PPA; metering 4–12 weeks | FED | Entirely national process; Victoria adds no state-specific requirement today. | 完全是全国程序，维州目前不加任何州级要求。 | https://djsir.vic.gov.au/priorities-and-initiatives/ai-mission-statement/sustainable-data-centre-action-plan
VIC | 8 | Construction, commissioning and energisation; local community and council dynamics | 建设、调试送电及地方社区动态 | Building permits are issued under the Building Act 1993 by a relevant building surveyor. - Energy Safe Victoria certificates and DNSP/AusNet commissioning tests (NER cl 5.7–5.8) precede energisation, which is usually staged. - Local opposition is rising: Hume City Council moved a data centre moratorium motion in August 2026 and councils have sought a greater say, which can slow council-pathway permits. - DFP permits are insulated from third-party appeal but not from political pressure. - Post-energisation obligations include planning permit conditions, the EPA general environmental duty and, once legislated, the national demand-flexibility and reporting standards. | 建筑许可依Building Act 1993由相关建筑测量师签发。 - 送电前须取得Energy Safe Victoria证书并完成DNSP/AusNet调试测试（NER cl 5.7–5.8），通常分阶段送电。 - 地方反对声音上升：Hume City Council 2026年8月提出数据中心暂停动议，各议会要求更大话语权，可能拖慢议会路径的许可。 - DFP许可不受第三方上诉影响，但躲不开政治压力。 - 送电后义务包括规划许可条件、EPA一般环境义务，以及立法后的全国需求灵活性与报告标准。 | Relevant building surveyor; Energy Safe Victoria; AusNet/DNSP; council (permit compliance) | Building Act 1993 (Vic); Electricity Safety Act 1998; NER cl 5.7–5.8 | Construction 18–30 months; commissioning 2–6 months per stage | FED | Commissioning follows national NER/AEMO procedures; the state adds building and electrical safety sign-offs. | 调试遵循全国NER/AEMO程序；州层面增加建筑及电气安全签核。 | https://datacentres.civicinterplay.io/sheets/vic ¦ https://councilmagazine.com.au/councils-seek-greater-say-on-data-centres
QLD | 1 | Site selection, zoning and pre-lodgement: social impact assessment and community benefit agreement (proposed) | 选址、分区及拟议社会影响评估前置 | Under the Planning Act 2016 the level of assessment is set by the local planning scheme and the Planning Regulation 2017. - Data centres are typically located in industry or special-industry zones and may be code assessable (no public notification) or impact assessable (public notification and third-party appeal to the Planning and Environment Court). - In August 2026 the Premier announced that data centre proponents must complete a social impact assessment and enter a community benefit agreement with the local council before lodging a DA, the same model imposed on wind and solar farms via the 2025 Planning (Social Impact and Community Benefit) Amendment. - The implementing regulation had not been made as of mid-September 2026. - Trade and Investment Queensland and the Department of State Development act as investment facilitators; there is no published Queensland data centre strategy. - On 2 October 2026 the Premier confirmed the social impact assessment and community benefit agreement must be completed before a development application is lodged, delivered through the renewable energy framework in place since July 2025; the amending regulation and size thresholds were still unpublished at 7 October 2026. | 依Planning Act 2016，评估级别由地方规划方案及Planning Regulation 2017确定。 - 数据中心一般落在工业区或特殊工业区，可能是代码评估（无需公告）或影响评估（需公告，第三方可向Planning and Environment Court上诉）。 - 2026年8月州长宣布，数据中心业主须在提交DA前完成社会影响评估并与地方议会签订社区利益协议，套用2025年Planning (Social Impact and Community Benefit) Amendment对风电、光伏项目的做法。 - 截至2026年9月中旬，实施条例尚未颁布。 - Trade and Investment Queensland及Department of State Development承担投资促进角色；昆州尚无公开的数据中心战略。 - 2026年10月2日州长确认，社会影响评估及社区利益协议须在提交开发申请前完成，沿用2025年7月起适用于可再生能源项目的框架；截至2026年10月7日修订条例与适用门槛仍未公布。 | Local government (assessment manager); Department of State Development, Infrastructure and Planning | Planning Act 2016 (Qld) ch 3; Planning Regulation 2017 (Qld) Sch 6–10; proposed extension of social impact assessment / community benefit agreement requirements to data centres (announced Aug 2026, not yet made) | 3–9 months including SIA if required | FED | FIRB and the Commonwealth data centre expectations apply concurrently; National Cabinet's land-use standards will overlay local scheme assessment once legislated. | FIRB及联邦数据中心期望框架同步适用；国家内阁土地利用标准立法后将叠加于地方规划方案评估。 | https://www.abc.net.au/news/2026-08-24/ai-data-centre-energy-rules-override-qld/107068536 ¦ https://www.legislation.qld.gov.au/view/pdf/inforce/current/act-2016-025 ¦ https://www.ashurstperkinscoie.com/en/insights/australia-evolving-data-centre-landscape-policy-meets-pipeline/
QLD | 2 | Development approval under the Planning Act 2016 (council DA with SARA referral) or coordinated project declaration | 开发批准（议会DA/SARA）或协调项目 | A development application is lodged with the council and proceeds through the Development Assessment Rules: confirmation, information request, public notification if impact assessable, decision. - State interests (main roads, environmentally relevant activities, electricity infrastructure easements) are referred to SARA under Schedule 10 of the Planning Regulation. - Decision periods are 35 business days after the information/notification stages, but large impact-assessable projects commonly take 9–18 months including appeals; the ABC reports the Western Downs Digital Park expects a multi-year council process. - Alternatively a proponent can ask the Coordinator-General to declare a 'coordinated project' under s 26 of the SDPWO Act, triggering a whole-of-government EIS or impact assessment report and letting the CG impose conditions. - The August 2026 SDPWO amendments define 'data centre' and exclude commercial and R&D data centres from the new 'State strategic project' designation (with its land-acquisition and modified-approval powers) unless ancillary to another project. - On 2 October 2026 Queensland announced that data centre applications will be assessed at State level through SARA rather than by councils, retaining public notification and third-party appeal; transitional treatment of applications already lodged, including Zerra's Kogan campus lodged 17 August 2026, has not been published. | DA向议会提交，按Development Assessment Rules推进：确认、信息请求、影响评估项目需公告、决定。 - 涉及州级利益的事项（主干道、环境相关活动、电力基础设施地役权）依Planning Regulation Schedule 10转介SARA。 - 信息/公告阶段结束后，法定决定期为35个工作日；但大型影响评估项目含上诉通常需9–18个月，ABC报道Western Downs Digital Park预期议会程序将持续数年。 - 另一路径是依SDPWO Act s 26申请Coordinator-General宣布为“coordinated project”，启动全政府EIS或影响评估报告，由CG设定条件。 - 2026年8月SDPWO修正案定义了“data centre”，并把商业及研发数据中心排除在新设“State strategic project”（含土地征用及修改审批权）之外，除非附属于其他项目。 - 2026年10月2日昆州宣布数据中心申请改由州级SARA评估而非地方议会，保留公告及第三方上诉权；已提交申请（含Zerra于2026年8月17日递交的Kogan园区）的过渡安排尚未公布。 | Local government / Planning and Environment Court; SARA; Coordinator-General (SDPWO Act) | Planning Act 2016 ch 3 pt 3; Development Assessment Rules; Planning Regulation 2017 Sch 10; State Development and Public Works Organisation Act 1971 s 26 (coordinated project); SDPWO (Critical Minerals) and Other Legislation Amendment Act 2026 (passed 26 Aug 2026) | Code assessable 3–6 months; impact assessable 9–18 months; coordinated project EIS 18–30 months | FED | The Queensland–Commonwealth bilateral agreement lets a coordinated-project EIS satisfy EPBC assessment; ordinary council DAs need a separate EPBC referral if triggered. | 昆州–联邦双边协议允许以coordinated project的EIS满足EPBC评估；普通议会DA如触发EPBC，须另行转介。 | https://www.minterellison.com/articles/major-reforms-to-fast-track-projects-in-queensland ¦ https://www.abc.net.au/news/2026-09-14/western-downs-digital-park-data-centre-energy-queensland/107115082 ¦ https://www.legislation.qld.gov.au/view/pdf/inforce/current/act-2016-025
QLD | 3 | Environmental authority for environmentally relevant activities (EP Act 1994) | 环境相关活动的环境授权（EP Act） | Data centre backup generation and fuel storage can constitute prescribed environmentally relevant activities under Schedule 2 of the Environmental Protection Regulation 2019. - Examples: ERA 14 electricity generation above the threshold using fuel, and fuel-burning/chemical storage thresholds. - These require an environmental authority from the Department of Environment and a concurrent ERA referral within the DA. - Noise and air-quality conditions are set through the EA and DA. - Water supply agreements with Seqwater/Urban Utilities or regional councils are commercial rather than statutory approvals, but are increasingly scrutinised given National Cabinet's water standard. | 数据中心的备用发电和燃油储存可能构成Environmental Protection Regulation 2019 Schedule 2规定的环境相关活动（ERA）。 - 例如ERA 14——超过门槛的燃料发电，以及燃烧/化学品储存门槛。 - 触发后须向环境部申领环境授权（EA），并在DA中同步进行ERA转介。 - 噪声及空气质量条件通过EA和DA设定。 - 与Seqwater/Urban Utilities或地区议会的供水协议属商业安排而非法定审批，但在国家内阁用水标准之下审视趋严。 | Department of the Environment, Tourism, Science and Innovation (Qld); SARA | Environmental Protection Act 1994 (Qld) ch 5; Environmental Protection Regulation 2019 Sch 2 (ERAs) | 3–6 months, concurrent with DA | FED | No federal equivalent unless EPBC is triggered. | 除触发EPBC外没有联邦对应程序。 | https://www.business.qld.gov.au/industries/mining-energy-water/energy/renewable/project-development/planning-approvals
QLD | 4 | Powerlink transmission connection: enquiry, application and Connections Guarantee timeframes | Powerlink输电接入及接入保证时限 | Loads above roughly 50–100 MW, or those near 110/132/275 kV substations, connect directly to Powerlink under NER Chapter 5. - Powerlink's Connection Application Guide covers enquiry, application, negotiation of a Connection and Access Agreement (C&AA), offer to connect and commissioning; the application stage runs 'notionally 12–18 months' depending on scope and acceptance of standard commercial terms, with AEMO evaluation fees passed through. - Under the Crisafulli Government's Energy Roadmap, Powerlink's Connections Guarantee commits to enquiry responses within 30 business days (40 for dedicated connection assets) per the NER. - It also commits to assessing 75% of performance-standard packages within 30 business days, negotiated access standard decisions within 30 business days of complete information, and 90% on-time delivery under executed agreements, explicitly covering transmission-connected loads. - Powerlink's 2025 TAPR flags data centres as a major driver of south-east Queensland demand. | 约50–100 MW以上、或邻近110/132/275 kV变电站的负荷，依NER第5章直接接入Powerlink。 - Powerlink的Connection Application Guide涵盖咨询、申请、Connection and Access Agreement（C&AA）谈判、接入报价及调试；申请阶段“名义上需12–18个月”，视范围及是否接受标准商业条款而定，AEMO评估费转嫁客户。 - 依Crisafulli政府Energy Roadmap，Powerlink的Connections Guarantee承诺按NER在30个工作日内回复咨询（专用接入资产40日）。 - 还承诺75%的性能标准包在30个工作日内完成评估、协商接入标准在资料齐备后30个工作日内决定、已签协议项目90%按时交付，明确涵盖输电接入负荷。 - Powerlink 2025年TAPR把数据中心列为昆州东南部需求增长的主要驱动。 | Powerlink Queensland (TNSP); AEMO (advisory matters) | NER cl 5.3.2–5.3.7, Schedule 5.3; Powerlink Connections Guarantee (Queensland Energy Roadmap, policy commitment) | Application stage 12–18 months; 2–3 years enquiry to energisation | FED | The Guarantee restates NER timeframes as state policy; performance standards for ≥30 MW inverter-based loads will follow the AEMC's ERC0394 final rule. | Connections Guarantee以州政策形式重申NER时限；30 MW及以上逆变器型负荷的性能标准将以AEMC ERC0394最终规则为准。 | https://www.powerlink.com.au/sites/default/files/2024-12/Connection%20Application%20Guide.pdf ¦ https://www.powerlink.com.au/connections-guarantee ¦ https://www.powerlink.com.au/sites/default/files/2025-12/Transmission%20Annual%20Planning%20Report%202025.pdf
QLD | 5 | Energex / Ergon large customer connection (NER Chapter 5A or 5) under the Large Customer Connection Manual | Energex/Ergon大客户配电接入 | Distribution-connected data centres (11–110 kV, typically up to ~60 MW) follow Energy Queensland's Large Customer Connection Manual (effective 5 January 2026). - Chapter 5A pathway: the DNSP acknowledges an enquiry within 5 business days, may require pre-application services, and aims to issue a negotiated connection offer within 65 business days of a complete application, to be accepted within 20 business days. - Chapter 5 pathway: preliminary response in 15 business days, detailed response in 30 business days, offer within four months. - Connection assets and large-customer extensions are alternative control services charged user-pays up front, with capital contributions for standard control augmentation outside the planning horizon. - Customers may design-construct-transfer connection assets or have the DNSP build-own-operate; financial security may be required. - The manual contains no data-centre-specific provisions. | 配网接入的数据中心（11–110 kV，一般不超过约60 MW）遵循Energy Queensland的Large Customer Connection Manual（2026年1月5日生效）。 - 第5A章路径：DNSP在5个工作日内确认咨询，可要求预申请服务，力争在完整申请后65个工作日内出具协商接入报价，客户须20个工作日内接受。 - 第5章路径：初步回复15个工作日、详细回复30个工作日、报价4个月内出具。 - 接入资产及大客户延伸线路属替代管制服务，用户预先付费；规划期以外的标准管制增容另收资本分摊。 - 客户可采用设计–建造–移交模式，或由DNSP建设–持有–运营；可能要求提供财务担保。 - 手册中没有针对数据中心的专门条款。 | Energex / Ergon Energy (Energy Queensland); AER (connection policy) | NER Chapter 5A Part D (negotiated connections) or Chapter 5; Energex/Ergon Connection Policies approved by AER; Large Customer Connection Manual (Jan 2026) | Offer 65 business days (Ch 5A) or 4 months (Ch 5); total 9–18 months | FED | Pure NER process; Queensland adds no state overlay beyond the Energy Roadmap service commitments. | 纯NER程序；除Energy Roadmap的服务承诺外，昆州未叠加州级规则。 | https://www.energex.com.au/__data/assets/pdf_file/0011/1090649/Large-Customer-Connection-Manual-3040635.pdf ¦ https://www.energex.com.au/our-services/connections/large-customer-connections/large-customer-electricity-connections
QLD | 6 | Connection and Access Agreement, augmentation and cost allocation | C&AA接入协议、增容与成本分担 | Powerlink's Connection and Access Agreement (the NER cl 5.3.7 connection agreement) prices connection assets as negotiated or prescribed transmission services. - Shared-network augmentation needed for a large load is assessed under the RIT-T (cl 5.16) and, if justified, recovered through Powerlink's regulated revenue from all Queensland customers. - The pending Commonwealth cost-recovery rule changes and National Cabinet standards aim to shift that cost to the data centre. - Queensland has not introduced NSW-style bonds or upgrade fees. - Government-owned generators (CS Energy, Stanwell, CleanCo) and Powerlink are being positioned to offer firmed supply, consistent with the state's energy-agnostic stance. | Powerlink的Connection and Access Agreement（即NER cl 5.3.7接入协议）将接入资产按协商或规定输电服务定价。 - 大负荷所需的共享网络增容依RIT-T（cl 5.16）评估，通过测试的经Powerlink受监管收入由全体昆州用户分摊。 - 联邦待审成本回收规则修改及国家内阁标准的目标，是把这部分成本转由数据中心承担。 - 昆州未引入新州式的保证金或升级费。 - 国有发电商（CS Energy、Stanwell、CleanCo）及Powerlink正被定位为可靠电力供应方，与该州能源技术中立立场一致。 | Powerlink / Energex / Ergon; AER | NER cl 5.3.7, 5.16 RIT-T, 5.17 RIT-D; Chapter 6A Part D; Chapter 5A Part E | 6–12 months to executed agreement | FED | Cost allocation is national; Queensland dissented from renewable-only sourcing but accepted the 'pay full network costs' national standard. | 成本分担属全国事项；昆州反对仅限可再生能源的供电要求，但接受了“全额支付网络成本”的全国标准。 | https://www.claytonutz.com/insights/2026/august/nine-governments-one-rulebook-national-cabinet-backs-mandatory-ai-and-data-centre-standards ¦ https://www.aemc.gov.au/rule-changes/cost-recovery-network-augmentations-package-1
QLD | 7 | Retailer/FRMP, AEMO registration and energy sourcing (energy-agnostic firming) | 零售商/FRMP、AEMO注册与技术中立供电 | A retailer is appointed as FRMP or the operator registers as a Market Customer with AEMO; metering follows NER Chapter 7. - Queensland argued at the July–August 2026 ECMC and National Cabinet meetings for a technology-agnostic approach. - Under the agreed national framework Queensland data centres may satisfy the firming requirement with coal or gas-backed contracts, while still needing new-generation REGO certificates once the Commonwealth legislates. - The Western Downs project cites nearby gas plants plus solar and wind. - AEMO registration of large facilities is expected 24–36 months after ministerial endorsement. | 指定零售商为FRMP，或由运营商向AEMO注册为Market Customer；计量遵循NER第7章。 - 昆州在2026年7–8月ECMC及国家内阁会议上力主技术中立。 - 在已达成的全国框架下，昆州数据中心可用煤电或燃气支撑的合约满足可靠容量要求，但联邦立法后仍须持有新建电源的REGO证书。 - Western Downs项目的供电方案提到附近燃气电厂加光伏、风电。 - 大型设施的AEMO注册预计在部长认可后24–36个月落地。 | Retailer/FRMP; AEMO | NER Chapter 2, Chapter 7; National Cabinet framework (26 Aug 2026) | 3–12 months | FED | National process; Queensland's carve-out changes what counts as firm capacity, not the NER registration mechanics. | 全国程序；昆州的例外只改变可靠容量的认定口径，不改变NER注册机制。 | https://www.abc.net.au/news/2026-09-14/western-downs-digital-park-data-centre-energy-queensland/107115082 ¦ https://www.abc.net.au/news/2026-08-24/ai-data-centre-energy-rules-override-qld/107068536
QLD | 8 | Construction, commissioning and energisation | 建设、调试与送电 | Building approvals are issued by a private certifier under the Building Act 1975; the Electrical Safety Act 2002 governs installation safety. - Powerlink or the DNSP witnesses commissioning under the connection agreement (NER cl 5.7–5.8). - The Connections Guarantee tracks on-time delivery. - Energisation is usually staged against consented capacity, with ongoing compliance against DA conditions and the environmental authority. | 建筑批准由私人审核员依Building Act 1975签发；Electrical Safety Act 2002规范安装安全。 - Powerlink或DNSP依接入协议见证调试（NER cl 5.7–5.8）。 - Connections Guarantee追踪按时交付情况。 - 送电通常按获批容量分阶段进行，并须持续遵守DA条件及环境授权。 | Private certifier; Electrical Safety Office; Powerlink / Energex / Ergon | Building Act 1975 (Qld); Electrical Safety Act 2002 (Qld); NER cl 5.7–5.8 | Construction 18–30 months; commissioning 2–6 months per stage | FED | Commissioning follows national NER/AEMO procedures; state adds building and electrical safety certification. | 调试遵循全国NER/AEMO程序；州层面增加建筑及电气安全认证。 | https://www.powerlink.com.au/connections-guarantee
WA | 1 | Site selection, zoning under local planning scheme and early Western Power capacity discussion | 选址、分区及Western Power早期沟通 | Data centre siting starts with confirming zoning permissibility and early network engagement before land is committed. - Under the Planning and Development (Local Planning Schemes) Regulations 2015 model provisions, data centres are generally 'industry' or 'telecommunications infrastructure' uses, permitted ('P') or discretionary ('D') in industrial zones of the relevant local planning scheme. - Some industrial estates (Kwinana, Kewdale, Malaga, Neerabup) are covered by structure plans or improvement schemes. - SWIS capacity is concentrated around Perth's 132 kV ring and the north-south 330 kV backbone, so proponents should lodge an early enquiry through Western Power's MyWPProjects portal and review its quarterly Major Customer Connections Insights Report before committing to land. - Native title and Aboriginal heritage due diligence under the Aboriginal Heritage Act 1972 (restored 2023) is also completed at this stage. | 选址阶段须先核实分区可行性，并在落实土地前尽早与电网对接。 - 依《2015年规划与发展（地方规划方案）条例》示范条款，数据中心一般归为“工业”或“电信基础设施”用途，在相关地方规划方案的工业区中属允许（P）或酌情（D）用途。 - 部分工业区（Kwinana、Kewdale、Malaga、Neerabup）适用结构规划或改善方案。 - SWIS容量集中在珀斯132 kV环网及南北向330 kV主干，业主应在确定土地前通过Western Power的MyWPProjects门户提交早期咨询，并查阅其季度《大客户接入洞察报告》。 - 原住民土地权及依《1972年原住民遗产法》（2023年恢复）的遗产尽职调查亦在此阶段完成。 | Local government; Department of Planning, Lands and Heritage; Western Power | Planning and Development Act 2005 (WA); Planning and Development (Local Planning Schemes) Regulations 2015; Aboriginal Heritage Act 1972 | 2–6 months | FED | FIRB screening and Commonwealth data centre expectations apply; National Cabinet standards will overlay WA planning once legislated. | FIRB审查及联邦数据中心期望框架适用；国家内阁标准立法后将叠加于西澳规划审批之上。 | https://www.westernpower.com.au/resources-education/industry-resources/large-industry-customers-and-generators/major-customer-connection-review/ ¦ https://www.westernpower.com.au/products-services/install-something-new/connect-my-home-or-business/distribution-loads--large-generators/
WA | 2 | Development approval: local government / DAP, or Significant Development Pathway (Part 11B) | 开发批准：地方政府/DAP或第11B部分路径 | Development approval runs through either the standard council/DAP track or the state-level fast-track pathway. - A development application is determined by local government, or by a Development Assessment Panel where estimated cost exceeds the DAP thresholds (mandatory above $10m in most areas, optional from $2m), within 60 or 90 days under the deemed provisions. - Since 1 March 2024, the permanent Significant Development Pathway (Part 11B, Planning and Development Act) lets projects of at least $20m in Perth/Peel (or $5m elsewhere) be determined by the WAPC's Statutory Planning Committee, which can override local scheme requirements. - The Committee targets a decision within 120 days, with a stop-the-clock mechanism; DPLH's guidance does not name data centres specifically, but they meet the cost test. - Review of a refusal lies only to the State Administrative Tribunal, and only the applicant may apply. | 开发批准可走标准的议会/DAP路径，或州级快速通道。 - 开发申请由地方政府裁定，或在预计成本超过DAP门槛时（多数地区1000万澳元以上强制、200万澳元起可选）由开发评估委员会裁定，依默示条款期限为60或90天。 - 自2024年3月1日起，永久性重大开发路径（《规划与发展法》第11B部分）允许珀斯/皮尔地区2000万澳元以上（其他地区500万澳元以上）的项目由WAPC法定规划委员会裁定，可凌驾地方方案要求。 - 该委员会以含暂停计时机制的120天为目标作出决定；DPLH指引未特别点名数据中心，但其符合成本测试。 - 对拒批的复审仅可向州行政法庭申请，且仅申请人有权提出。 | Local government or Development Assessment Panel; WAPC Statutory Planning Committee (Part 11B) | Planning and Development Act 2005 (WA) Part 11B (Significant Development Pathway), Part 17 (closed); Planning and Development (Development Assessment Panels) Regulations 2011; Planning and Development (Local Planning Schemes) Regulations 2015 Sch 2 deemed provisions | DAP 90 days; Part 11B 120-day target; 6–12 months in practice | FED | EPBC referral, if triggered, is coordinated under the WA–Commonwealth bilateral assessment agreement; otherwise a purely state approval. | 如触发EPBC评估，依西澳–联邦双边评估协议协调办理；否则纯属州级审批。 | https://www.planning.wa.gov.au/significant-development-pathway
WA | 3 | Environmental approvals: EPA referral (EP Act Part IV) and DWER works approval/licence (Part V) | 环境审批：EPA转介及DWER许可 | Environmental clearance covers EPA referral and DWER licensing for large backup generation. - Proposals likely to significantly affect the environment may be referred to the WA EPA under s 38 of the Environmental Protection Act 1986; most metropolitan data centres are not formally assessed, but large greenfield campuses involving clearing or major water demand can be. - Prescribed premises under Schedule 1 of the Environmental Protection Regulations 1987 (e.g. category 52, fuel-fired electricity generation above 10 MW) need a works approval and licence from DWER for large diesel/gas backup fleets. - Water Corporation servicing agreements are required, and groundwater use needs a licence under the Rights in Water and Irrigation Act 1914. | 环境审批涵盖EPA转介及DWER对大型备用发电的许可。 - 可能对环境产生重大影响的提案可依《1986年环境保护法》第38条转介西澳EPA；多数都市数据中心不作正式评估，但涉及清理或大量用水的大型新开发园区可能需要。 - 属于《1987年环境保护条例》附表1规定场所的（如类别52——超过10 MW的燃料发电）大型柴油/燃气备用机组需向DWER申领工程批准及许可。 - 须与水务公司签订服务协议，使用地下水的还需依《1914年水权与灌溉法》申领许可。 | WA EPA; Department of Water and Environmental Regulation (DWER) | Environmental Protection Act 1986 (WA) Part IV (s 38 referral) and Part V (works approvals, licences); Environmental Protection Regulations 1987 Sch 1 | Part V works approval 3–6 months; Part IV assessment 12–24 months if required | FED | WA's Part IV assessment is accredited under the EPBC bilateral agreement, so a single assessment can serve both levels. | 西澳第IV部分评估已获EPBC双边协议认可，单一评估即可同时满足两级要求。 | https://www.planning.wa.gov.au/significant-development-pathway
WA | 4 | Western Power access application: enquiry, Applications and Queuing Policy, access offer (Electricity Networks Access Code 2004) | Western Power接入申请与报价 | Access proceeds through Western Power's major-customer process from enquiry to offer. - The process applies to distribution loads of 10 MVA or more and to all transmission-connected loads: enquiry via MyWPProjects, a fee-based preliminary/feasibility study, a formal access application under Chapter 5 of the Electricity Networks Access Code 2004. - The application is placed in a queue and processed under the ERA-approved Applications and Queuing Policy, with network studies run against the ERA-approved Technical Rules. - An access offer follows, leading to an Electricity Transfer Access Contract (ETAC) and a Customer Access Contract. - Western Power's Major Customer Connection Review produced an updated Major Customer Connection Process (June 2026) and quarterly Insights Reports; no published stage timeframes exist, but enquiry-to-offer for a transmission load runs 12–24 months in practice. - The State's DER and connections reform issues paper (20 July 2026) also touches network capacity sharing. | 接入按Western Power大客户程序从咨询走到报价。 - 该程序适用于10 MVA及以上配电负荷及所有输电接入负荷：通过MyWPProjects提交咨询、付费开展初步/可行性研究、依《2004年电力网络接入守则》第5章提交正式接入申请。 - 申请进入队列，依ERA批准的《申请与排队政策》处理，网络研究按ERA批准的《技术规则》进行。 - 随后发出接入报价，进而签订电力传输接入合同（ETAC）及客户接入合同。 - Western Power大客户接入审查形成了更新的《大客户接入程序》（2026年6月）及季度《洞察报告》；未公布各阶段时限，实践中输电负荷从咨询到报价需12–24个月。 - 州政府2026年7月20日的DER与接入改革议题文件也涉及网络容量共享。 | Western Power (network operator); Economic Regulation Authority (Access Code, Technical Rules, Applications and Queuing Policy) | Electricity Networks Access Code 2004 (WA) Chapter 5 (applications and queuing), Chapter 6 (contributions), Technical Rules (ss 12.1–12.3); Electricity Industry Act 2004 Part 8 | 12–24 months enquiry to access offer for transmission loads | FED | The NER does not apply; the Access Code is the WA equivalent of NER Chapter 5. Commonwealth data centre standards (registration, firm capacity) will need WEM-specific implementation. | NER不适用；《接入守则》是西澳版的NER第5章。联邦数据中心标准（注册、可靠容量）须在WEM中另行落实。 | https://www.westernpower.com.au/resources-education/industry-resources/large-industry-customers-and-generators/major-customer-connection-review/ ¦ https://www.westernpower.com.au/products-services/install-something-new/connect-my-home-or-business/transmission-connected-loads-generators/ ¦ https://www.wa.gov.au/system/files/2026-07/issues-paper-der-data-and-connections-reform.pdf
WA | 5 | Network augmentation and capital contributions (Contributions Policy, Chapter 6 of the Access Code) | 网络扩建与资本分摊 | Cost allocation is governed by the Access Code's contributions regime rather than a RIT-T-style test. - Under Chapter 6 of the Access Code and Western Power's ERA-approved Contributions Policy, the applicant pays a capital contribution for connection assets and for shared-network augmentation whose cost exceeds the incremental revenue Western Power expects from the load over the regulatory period (the 'new facilities investment test', s 6.52). - Western Power may offer non-standard or 'flexible' connections where the customer accepts curtailment; deposits or bank guarantees are commonly required. - There is no RIT-T; major augmentations are instead justified through Western Power's Access Arrangement (AA6, 2027–2032, currently under ERA review) and the Whole of System Plan. | 成本分担依《接入守则》分摊机制办理，而非RIT-T式测试。 - 依《接入守则》第6章及Western Power经ERA批准的《分摊政策》，申请人须为接入资产及成本超过Western Power预期在监管期内从该负荷获得的增量收入的共享网络扩建支付资本分摊（第6.52条“新设施投资测试”）。 - Western Power可在客户接受限电的情况下提供非标准或“灵活”接入，通常要求缴纳保证金或银行担保。 - 西澳没有RIT-T；重大扩建改为通过Western Power的《接入安排》（AA6，2027–2032年，目前由ERA审查中）及《全系统规划》论证。 | Western Power; ERA | Electricity Networks Access Code 2004 Chapter 6 (ss 6.40–6.60 contributions, new facilities investment test); Western Power Contributions Policy | Determined with the access offer | FED | The Commonwealth's 'pay full network costs' standard largely mirrors existing WA practice, where contributions already fall on the causer. | 联邦“全额支付网络成本”标准与西澳现行做法基本一致，后者已由引起成本的一方承担分摊。 | https://www.westernpower.com.au/products-services/install-something-new/connect-my-home-or-business/distribution-loads--large-generators/
WA | 6 | WEM arrangements: retailer / Market Customer registration and Reserve Capacity | WEM安排：零售商注册与备用容量 | Market arrangements run through WEM registration and the Reserve Capacity Mechanism rather than the NEM. - Electricity is bought from Synergy or a contestable retailer (customers above 50 MWh/yr are contestable), or the operator registers with AEMO as a Market Participant/Market Customer under the WEM Rules. - Under the Reserve Capacity Mechanism, the serving retailer must hold Capacity Credits equal to its Individual Reserve Capacity Requirement, assigned two years ahead, so a 100+ MW step change must be flagged early to AEMO's WA forecasting team and the retailer, or the market risks a capacity shortfall and elevated Reserve Capacity Prices. - Large loads may also register as Demand Side Programmes to earn capacity payments for curtailability. - Data centres face no WA-specific registration obligation today; AEMO counts 15 operating WA data centres. | 市场安排依WEM注册及备用容量机制办理，而非NEM。 - 电力从Synergy或可竞争零售商购买（年用电量超过50 MWh的客户可自由选择），或由运营商依WEM规则向AEMO注册为市场参与者/市场客户。 - 依备用容量机制，供电零售商须持有与其个体备用容量要求相等的容量信用，该要求提前两年分配，因此100 MW以上的负荷跃升须及早告知AEMO西澳预测团队及零售商，否则市场可能面临容量短缺及备用容量价格上升。 - 大负荷也可注册为需求侧计划，凭可削减性获得容量收益。 - 数据中心目前不面临任何西澳特有的注册义务；AEMO统计西澳有15个运营中的数据中心。 | AEMO (WEM operator); ERA; Synergy / contestable retailers | Wholesale Electricity Market Rules (WA) Chapter 2 (registration) and Chapter 4 (Reserve Capacity Mechanism, Individual Reserve Capacity Requirements); Electricity Industry Act 2004; Electricity Corporations Act 2005 | Retail contracting 3–9 months; capacity year cycle 2 years ahead | FED | The AEMC's advice applies to the NEM; implementing REGO/firm-capacity and registration standards in the WEM will require separate WA rule changes by the Coordinator of Energy. | AEMC的建议适用于NEM；在WEM中落实REGO/可靠容量及注册标准，须由能源协调官另行修改西澳规则。 | https://www.aemo.com.au/newsroom/news-updates/digital-demand-surge ¦ https://www.ashurstperkinscoie.com/en/insights/australian-electricity-and-gas-markets-july-2026-update/
WA | 7 | Metering, commissioning and energisation (Metering Code, Technical Rules, Building and Energy) | 计量、调试与送电 | Energisation requires metering approval, electrical safety sign-off and commissioning witness. - Western Power installs or approves metering under the Electricity Industry (Metering) Code 2012; installations must comply with the Technical Rules and WA Electrical Requirements. - Building and Energy (Electrical Inspectors) must be satisfied before energisation. - Western Power witnesses commissioning of transmission connection assets and may impose staged energisation and ramp constraints under the ETAC where system studies show voltage or stability limits. - The Coordinator of Energy's 2026 reform work also considers minimum state-of-charge and storage obligations that could affect co-located BESS. | 送电前须完成计量核准、电气安全签核及调试见证。 - Western Power依《2012年电力工业（计量）守则》安装或批准计量装置；安装须符合《技术规则》及西澳电气要求。 - 送电前须获Building and Energy（电气检查员）认可。 - Western Power见证输电接入资产调试，系统研究显示存在电压或稳定性限制时，可依ETAC施加分阶段送电及爬坡约束。 - 能源协调官2026年的改革工作也在考虑可能影响共址储能的最低荷电状态及储能义务。 | Western Power; Building and Energy (DEMIRS); AEMO (system operator) | Electricity Industry (Metering) Code 2012 (WA); Technical Rules; Electricity (Licensing) Regulations 1991 | Commissioning 2–6 months per stage |  | Entirely WA-regulated; no NER/AEMO NEM commissioning procedures apply. | 完全由西澳监管；不适用NER/AEMO的NEM调试程序。 | https://www.westernpower.com.au/products-services/install-something-new/connect-my-home-or-business/transmission-connected-loads-generators/
SA | 1 | Site selection, Planning and Design Code zoning and Coordinator-General / Invest SA engagement | 选址、《规划与设计准则》分区及总协调官对接 | Siting rests on the Planning and Design Code's zone rules plus early Coordinator-General case management. - Under the PDI Act, the Planning and Design Code sets zone-based rules; data centres fit as 'industry'/'data centre'-type uses within Strategic Employment, Employment and Infrastructure zones. - Greenfield sites in the Mid North or Upper Spencer Gulf, near ElectraNet's 275 kV network and the proposed Northern Water desalination pipeline, are being actively promoted. - The Coordinator-General's Office for Major Projects and the Department of State Development case-manage large investments; the June 2026 strategy requires future applications to include SA Water confirmation of sufficient water availability. - Native title and Aboriginal Heritage Act 1988 clearances are handled at this stage. | 选址取决于《规划与设计准则》的分区规则，并配合总协调官的早期个案管理。 - 依PDI法，《规划与设计准则》设定基于分区的规则；数据中心以“工业”/“数据中心”类用途落入战略就业、就业及基础设施区。 - 州政府正积极推广中北部或上斯宾塞湾的新开发场址，该区域靠近ElectraNet 275 kV网络及拟建的北部海水淡化输水管。 - 总协调官的重大项目办公室及州发展部对大型投资进行个案管理；2026年6月战略要求未来申请须附SA Water确认有充足供水。 - 原住民土地权及《1988年原住民遗产法》审批在此阶段办理。 | PlanSA / State Planning Commission; Coordinator-General; Invest SA | Planning, Development and Infrastructure Act 2016 (SA); Planning and Design Code (zone policies); Aboriginal Heritage Act 1988 | 2–6 months | FED | FIRB and Commonwealth expectations run in parallel; SA promotes itself as aligned with the federal renewable-backed model. | FIRB审查及联邦期望框架并行推进；南澳以契合联邦可再生能源支撑模式作为卖点。 | https://www.abc.net.au/news/2026-06-23/sa-push-for-ai-data-centres-in-sa-in-new-strategy/106830536 ¦ https://w.media/south-australia-proposes-dedicated-data-centre-legislation/
SA | 2 | Development approval under the PDI Act: State Planning Commission 'essential infrastructure' pathway (and proposed Data Centre and AI Infrastructure Act) | 开发批准：州规划委员会"基础设施"路径 | Data centres are assessed on an essential-infrastructure track rather than through ordinary council processes. - Since late 2025, the State Planning Commission (through SCAP), not a council assessment panel, has been the relevant authority for major data centre proposals. - Applications are lodged on the PlanSA portal, assessed against the Code as performance-assessed development with public notification where required, and decided within the statutory 8–12 week period, extended where referred to the EPA, SA Water, ElectraNet/SAPN and the Technical Regulator. - The June 2026 strategy proposes a Data Centre and AI Infrastructure Act giving the Coordinator-General decision power over major projects and reducing duplication; the Bill's text, thresholds and timing remained unpublished as of September 2026. - Proposals with major environmental implications can instead be declared 'impact assessed development' under s 108, requiring an EIS and a Ministerial decision. - At 7 October 2026 the Data Centre and AI Infrastructure Bill had still not been introduced, and the AI Royal Commission terms of reference signed on 1 October 2026 expressly exclude data centre matters, leaving the PDI Act essential infrastructure pathway as the only operative route. | 数据中心走基础设施类评估路径，而非常规议会审批程序。 - 自2025年底起，州规划委员会（通过SCAP）而非议会评估委员会成为重大数据中心提案的相关审批机构。 - 申请在PlanSA门户提交，作为绩效评估开发依准则评估，准则要求时须公告，并在法定8–12周内决定，转介EPA、SA Water、ElectraNet/SAPN及技术监管官时延长。 - 2026年6月战略拟出台《数据中心与AI基础设施法》，赋予总协调官对重大项目的决定权并减少重复审批；截至2026年9月法案文本、门槛及时间表仍未公布。 - 具有重大环境影响的提案可依第108条改为宣布“影响评估开发”，须编制EIS并由部长决定。 - 截至2026年10月7日，Data Centre and AI Infrastructure Bill仍未提交州议会；2026年10月1日签署的AI Royal Commission职权范围明确排除数据中心事项，PDI Act基础设施路径仍是唯一可用途径。 | State Planning Commission / State Commission Assessment Panel; Minister for Planning (impact assessed); proposed Coordinator-General role | Planning, Development and Infrastructure Act 2016 (SA) ss 102–110 (assessment pathways), s 108 (impact assessed development); Planning and Design Code; proposed Data Centre and AI Infrastructure Act (announced 23–24 June 2026, not yet introduced) | 3–9 months for performance-assessed; 12–24 months if impact assessed | FED | EPBC referral, if triggered, is coordinated under the SA bilateral agreement; National Cabinet standards will overlay once legislated, with SA presenting its Act as the state implementation vehicle. | 如触发EPBC评估，依南澳双边协议协调办理；国家内阁标准立法后将叠加，南澳拟将其法案定位为州级落实载体。 | https://www.ashurstperkinscoie.com/en/insights/australia-evolving-data-centre-landscape-policy-meets-pipeline/ ¦ https://w.media/south-australia-proposes-dedicated-data-centre-legislation/ ¦ https://www.abc.net.au/news/2026-06-23/sa-push-for-ai-data-centres-in-sa-in-new-strategy/106830536
SA | 3 | Environmental licensing (EPA), water supply confirmation (SA Water) and Technical Regulator certification | 环境许可、供水确认及技术监管官认证 | Environmental, water and technical-compliance sign-offs run alongside planning. - Backup generation above the Schedule 1 thresholds of the Environment Protection Act 1993 (fuel-burning/electricity generation activities) requires an EPA licence; the EPA is a mandatory referral body for noise and air. - The June 2026 strategy requires SA Water confirmation of available supply as part of the application, a point made politically salient by the IREN Bundey proposal. - It also requires 'certification from the Technical Regulator that projects comply with the requirements of the state's power system', an SA-specific step under the Electricity Act 1996 with no NEM equivalent. - Electrical installations additionally need OTR certificates of compliance before energisation. | 环境、供水及技术合规签核与规划审批同步进行。 - 超过《1993年环境保护法》附表1门槛的备用发电（燃烧/发电活动）需EPA许可；EPA是噪声及空气方面的强制转介机构。 - 2026年6月战略要求申请中须附SA Water供水确认，该要求因IREN Bundey提案而具有政治敏感性。 - 战略还要求“技术监管官出具项目符合本州电力系统要求的认证”，这是依《1996年电力法》设立的南澳特有步骤，NEM中无对应程序。 - 电气装置在送电前还须取得OTR合规证书。 | SA EPA; SA Water; Office of the Technical Regulator | Environment Protection Act 1993 (SA) Sch 1 and Part 6; Electricity Act 1996 (SA) Part 4 (technical regulation) and s 60 (installation compliance); SA data centre strategy (June 2026) | 3–6 months, concurrent with development assessment | FED | The Technical Regulator certification sits alongside, not instead of, AEMO/ElectraNet performance-standard approval under the NER. | 技术监管官认证与NER下AEMO/ElectraNet的性能标准审批并行，而非替代。 | https://w.media/south-australia-proposes-dedicated-data-centre-legislation/
SA | 4 | ElectraNet transmission connection: pre-feasibility, enquiry and application (New Customer Connection Guide, March 2026) | ElectraNet输电接入：咨询与申请 | ElectraNet's Getting Connected guide sets a six-stage transmission connection process with explicit system-strength rules. - The guide (v1, 30 March 2026) covers pre-feasibility/enquiry (cl 5.3.2, with a template response), application to connect (cl 5.3.4, using a dedicated 'Application to Connect Loads' form), offer to connect (cl 5.3.5), connection agreement execution, design/build/registration and compliance testing. - Loads must propose Customer performance standards under Schedule 5.3 (S5.3.5, S5.3.11 are AEMO advisory matters). - Inverter-based loads must supply PSS/E and PSCAD models with DMAT results and undergo a system strength impact assessment under cl 5.3.4B, choosing between self-remediation or a system strength charge (SSC = SSUP × SSL × SSQ). - Stability assessments take about 6 to 12 weeks ('start when ready'). - ElectraNet's Assessment of Network Capacity for Connections report (June 2025) sets out available 275/132 kV headroom by region. | ElectraNet《接入指南》设定含明确系统强度规则的六阶段输电接入流程。 - 指南（v1，2026年3月30日）涵盖预可行性/咨询（第5.3.2条，附回复模板）、接入申请（第5.3.4条，使用专门的“负荷接入申请”表格）、接入报价（第5.3.5条）、接入协议签署、设计/建设/注册及合规测试。 - 负荷须依附表5.3提出客户性能标准（S5.3.5、S5.3.11为AEMO咨询事项）。 - 逆变器型负荷须提供PSS/E和PSCAD模型及DMAT结果，并依第5.3.4B条接受系统强度影响评估，可选择自行整治或支付系统强度费（SSC = SSUP × SSL × SSQ）。 - 稳定性评估约需6至12周（“就绪即启动”）。 - ElectraNet《接入网络容量评估报告》（2025年6月）按区域列出275/132 kV可用裕度。 | ElectraNet (TNSP); AEMO (advisory matters, system strength) | NER cl 5.3.2, 5.3.4, 5.3.4A, 5.3.4B, 5.3.5; Schedule 5.3 (S5.3.5, S5.3.11); ElectraNet Getting Connected guide (Mar 2026) | Enquiry 30–40 business days; application to offer 9–15 months | FED | Pure NER Chapter 5 process; the ERC0394 large-IBL standards will apply to ≥30 MW data centres from the final rule's commencement. | 纯NER第5章程序；ERC0394大型逆变器型负荷标准将自最终规则生效起适用于30 MW及以上数据中心。 | https://electranet.com.au/wp-content/uploads/2026/04/New-Customer-Connection-Guide-V1.pdf ¦ https://electranet.com.au/wp-content/uploads/2025/08/Electranet-Assessment-of-Network-Capacity-for-Connection-Report-2029-For-publishing.pdf ¦ https://electranet.com.au/services/connection-journey/
SA | 5 | SA Power Networks distribution connection (Manual 18: Connections & Ancillary Network Services, June 2026) | SA Power Networks配电接入（第18号手册） | Smaller loads connect to SA Power Networks under NER Chapter 5A, with Manual 18 setting the local process. - Loads up to roughly 30–60 MW connect at 11/33/66 kV under NER Chapter 5A Part D (negotiated connection, offer within 65 business days of a complete application), or Chapter 5 for the largest sites. - SAPN's Manual 18 (issued June 2026) sets out enquiry, application, offer and ancillary service fees. - SAPN's AER-approved Connection Policy governs capital contributions for connection assets and for augmentation beyond the planning horizon. - SAPN operates the Essential Services Commission's Electricity Distribution Code and is a referral body for planning applications affecting its network. | 较小负荷依NER第5A章接入SA Power Networks，第18号手册规定本地流程。 - 约30–60 MW以下负荷依NER第5A章D部分（协商接入，完整申请后65个工作日内报价）以11/33/66 kV接入，最大型场址则走第5章。 - SAPN第18号手册（2026年6月发布）规定了咨询、申请、报价及辅助服务费用。 - SAPN经AER批准的《接入政策》规范接入资产及规划期以外扩建的资本分摊。 - SAPN执行基本服务委员会的《配电守则》，并是影响其网络的规划申请的转介机构。 | SA Power Networks (DNSP); AER; ESCOSA | NER Chapter 5A Part D and Part E; SAPN Connection Policy (AER 2025–30 determination); SAPN Manual 18 (June 2026); Electricity Distribution Code (ESCOSA) | Offer 65 business days; total 9–15 months | FED | Pure NER process with no SA-specific overlay to date. | 纯NER程序，目前无南澳特有的叠加规则。 | https://www.sapowernetworks.com.au/public/download.jsp?id=337829 ¦ https://www.aer.gov.au/industry/networks/entities/assets/sa-power-networks-electricity-distribution-network
SA | 6 | Offer, connection agreement, augmentation and cost allocation | 接入报价、协议、扩建与成本分担 | Cost allocation follows NER offer/agreement mechanics, with system strength charges an SA-specific add-on. - The offer to connect (cl 5.3.6) and Transmission Connection Agreement (cl 5.3.7) allocate connection assets and dedicated connection assets to the applicant as negotiated transmission services. - Shared augmentation (e.g. new 275 kV capacity in the Mid North tied to the Northern Transmission Project, or Project EnergyConnect headroom) is subject to the RIT-T (cl 5.16) and regulated recovery, unless pending Commonwealth cost-recovery rules assign it to the load instead. - System strength charges under cl 5.3.4B are an additional SA-specific cost. - The State strategy stresses that data centres 'must secure their own power supply' under a user-pays system with no subsidies. | 成本分担依NER报价/协议机制办理，系统强度费是南澳特有附加成本。 - 接入报价（第5.3.6条）及输电接入协议（第5.3.7条）将接入资产和专用接入资产作为协商输电服务分配给申请人。 - 共享扩建（如与北部输电项目相关的中北部新275 kV容量，或EnergyConnect项目裕度）须经RIT-T（第5.16条）并由受监管收入回收，除非待审的联邦成本回收规则改为将其分配给负荷。 - 第5.3.4B条下的系统强度费是南澳特有的额外成本。 - 州战略强调数据中心“须自行确保电力供应”，采用用户付费、不设补贴的制度。 | ElectraNet / SAPN; AER | NER cl 5.3.6–5.3.7, 5.16 RIT-T, 5.3.4B system strength; Chapter 6A Part D | 6–12 months to executed agreements | FED | National cost-allocation rules apply; SA has not proposed NSW-style state bonds or fees. | 适用全国成本分担规则；南澳未提议新州式的州级保证金或费用。 | https://electranet.com.au/wp-content/uploads/2026/04/New-Customer-Connection-Guide-V1.pdf ¦ https://www.abc.net.au/news/2026-06-23/sa-push-for-ai-data-centres-in-sa-in-new-strategy/106830536
SA | 7 | Retailer/FRMP, AEMO registration, metering and renewable sourcing | 零售商/FRMP、AEMO注册与可再生采购 | Retail and registration follow the standard national process, with SA framing its renewable grid as a compliance advantage. - A retailer licensed by ESCOSA is appointed as FRMP, or the operator registers with AEMO directly as a Market Customer; metering follows NER Chapter 7. - SA's pitch is that its renewable-heavy grid makes compliance with the coming REGO/new-firm-capacity national standard straightforward. - SA has not yet published binding PPA metrics like NSW's. - Large flexible loads may also be attractive to AEMO for SA's system security needs; wholesale demand response or scheduled-load classification is optional today. | 零售与注册遵循全国标准程序，南澳将其可再生电网作为合规优势。 - 由持有ESCOSA牌照的零售商担任FRMP，或运营商直接向AEMO注册为市场客户；计量遵循NER第7章。 - 南澳的卖点是其高比例可再生电网使遵守即将出台的REGO/新增可靠容量全国标准较为容易。 - 南澳尚未像新州那样公布约束性PPA指标。 - 大型灵活负荷对AEMO应对南澳系统安全需求也具吸引力；目前参与批发需求响应或可调度负荷分类为自愿。 | Retailer/FRMP; AEMO; ESCOSA | NER Chapter 2 and 7; Electricity Act 1996 (SA) retail licensing | 3–9 months | FED | National process; SA adds no state requirement beyond retail licensing. | 全国程序；除零售牌照外南澳未增加州级要求。 | https://www.abc.net.au/news/2026-06-23/sa-push-for-ai-data-centres-in-sa-in-new-strategy/106830536
SA | 8 | Construction, R2/compliance testing, OTR sign-off and energisation | 建设、合规测试、OTR签核与送电 | Final steps combine building consent, R2-style testing and technical sign-off before full capacity is released. - Building consent is granted under the PDI Act by a council or private certifier. - ElectraNet's guide requires compliance and on-system testing (Schedule 5.5.2(b)-style R2 testing), with AEMO-endorsed test plans for large inverter-based loads, before full release of capacity. - OTR certificates of compliance are required for the installation. - Energisation is normally staged, with model validation carried out after each stage. | 投运前的收尾环节包括建筑许可、R2式测试及技术签核，全部容量分阶段释放。 - 建筑许可依PDI法由议会或私人审核员发放。 - ElectraNet指南要求大型逆变器型负荷在全部容量释放前完成合规及在网测试（类似附表5.5.2(b)的R2测试），测试方案须经AEMO认可。 - 装置须取得OTR合规证书。 - 送电通常分阶段进行，每阶段后进行模型验证。 | ElectraNet / SAPN; AEMO; Office of the Technical Regulator; building certifier | NER cl 5.7–5.8, Schedule 5.5; PDI Act 2016 Part 7 Div 1 (building consent); Electricity Act 1996 (SA) s 60 | Commissioning 2–6 months per stage | FED | NER/AEMO testing is national; OTR certification is the SA-specific addition. | NER/AEMO测试属全国程序；OTR认证是南澳特有的附加环节。 | https://electranet.com.au/wp-content/uploads/2026/04/New-Customer-Connection-Guide-V1.pdf
TAS | 1 | Site selection, Coordinator-General engagement and Draft Expectations alignment | 选址、总协调官对接及与期望草案对齐 | Proponents typically engage the Coordinator-General first, then align with the Draft Expectations and confirm zoning. - The Office of the Coordinator-General case-manages investment and holds a confidential pipeline; the Examiner reports many proponents had not yet engaged TasNetworks or generators, which the Government now expects to happen early. - The Draft Expectations (7 September 2026) ask proponents to support additional renewable generation, pay their share of network and connection costs, use water responsibly, engage communities, and follow standard approvals with no automatic approvals. - Zoning under the Tasmanian Planning Scheme (General or Light Industrial, or Utilities zone) is checked at this stage. - The 2018 Data Centre Action Strategy remains the only sector strategy document. - Consultation on the Draft Expectations closes 12 October 2026, feedback is analysed during October and the final Expectations are to be released by end-2026. | 业主通常先接触总协调官，再对齐期望草案要求并核查分区。 - 总协调官办公室对投资进行个案管理并持有保密项目储备；据《审查者报》报道，许多业主尚未接触TasNetworks或发电商，州政府现期望其尽早接洽。 - 《期望草案》（2026年9月7日）要求业主支持新增可再生发电、支付其应分摊的网络及接入成本、负责任用水、与社区沟通，并遵循标准审批、不设自动批准。 - 此阶段核查《塔州规划方案》分区（一般或轻工业区，或公用设施区）。 - 2018年《数据中心行动战略》仍是唯一的行业战略文件。 - 《期望草案》意见征集于2026年10月12日截止，10月内完成反馈分析，最终版预计2026年底发布。 | Office of the Coordinator-General; Department of State Growth; local planning authority | Land Use Planning and Approvals Act 1993 (Tas); Tasmanian Planning Scheme (State Planning Provisions zones); Draft Expectations for Data Centres and AI Infrastructure Developers (Sept 2026, non-statutory) | 2–6 months | FED | The Tasmanian Expectations mirror the Commonwealth's March 2026 expectations and National Cabinet standards; FIRB applies to foreign proponents. | 塔州期望框架与联邦2026年3月期望及国家内阁标准相呼应；FIRB适用于外国业主。 | https://www.premier.tas.gov.au/latest-news/2026/september/clear-expectations-for-data-centres-and-ai-infrastructure ¦ https://www.examiner.com.au/story/9346904/secret-tassie-ai-data-centre-plans-exposed-in-new-document/ ¦ https://www.cg.tas.gov.au/investment_opportunities/sector_opportunities/emerging_sectors/data_centres
TAS | 2 | Planning permit under LUPAA: council pathway or Major Projects declaration | LUPAA规划许可：议会路径或重大项目宣布 | Approval runs through either a council permit or the state Major Projects declaration. - A discretionary permit application is lodged with the council under s 57 of LUPAA (42-day statutory decision period after validity, extendable), with public advertising and appeal rights to the Tasmanian Civil and Administrative Tribunal. - For projects of state significance or spanning several municipalities, the proponent can ask the Minister for Planning to declare a 'major project' under LUPAA Part 4 Division 2A. - The Tasmanian Planning Commission then convenes a Development Assessment Panel that issues assessment criteria, coordinates EPA, TasWater and heritage approvals, and decides within about 12–18 months, with no merits appeal. - Council-level concern over energy and water is rising following the September 2026 disclosures. | 审批走议会许可路径或州级重大项目宣布路径。 - 依LUPAA第57条向议会提交酌情许可申请（有效后42天法定决定期，可延长），须公告并可向塔州民事与行政法庭上诉。 - 对于具有州级重要性或跨多个市政区的项目，业主可申请规划部长依LUPAA第4部分第2A分部宣布为“重大项目”。 - 此后塔州规划委员会组建开发评估委员会，发布评估标准，协调EPA、TasWater及遗产审批，并在约12–18个月内决定，无实体上诉。 - 2026年9月信息披露后，议会层面对能源及用水的关注正在上升。 | Local planning authority (council) / TASCAT; Minister for Planning and Tasmanian Planning Commission DAP (Major Projects) | Land Use Planning and Approvals Act 1993 (Tas) s 57 (discretionary permits), Part 4 Division 2A (Major Projects, inserted 2020) | Council 3–9 months incl. appeals; Major Project 12–18 months | FED | EPBC matters can be assessed through the Tasmanian bilateral agreement; National Cabinet standards will overlay once legislated. | EPBC事项可通过塔州双边协议评估；国家内阁标准立法后将叠加。 | https://www.examiner.com.au/story/9346904/secret-tassie-ai-data-centre-plans-exposed-in-new-document/ ¦ https://www.abc.net.au/news/2026-09-09/six-new-confidential-data-centre-proposals-tasmania-revealed/107131974
TAS | 3 | Environmental assessment by EPA Tasmania (EMPCA Level 2 activities) | 塔州EPA环境评估（EMPCA二级活动） | Level 2 activities trigger a mandatory EPA referral alongside the planning permit. - Where a project includes a Level 2 activity under Schedule 2 of EMPCA 1994 (e.g. fuel-burning/electricity generation above the threshold, or large fuel storage), the council must refer the permit application to the EPA Board. - The EPA Board assesses the referral, often requiring an Environmental Effects Report or EIS, and issues environmental conditions binding on the permit. - TasWater servicing and Hydro Tasmania water-licence issues arise where cooling-water demand is significant. | 二级活动触发向EPA的强制转介，与规划许可同步办理。 - 项目若含《1994年环境管理与污染控制法》附表2列明的二级活动（如超过门槛的燃烧/发电或大型燃油储存），议会须将许可申请转交EPA董事会。 - EPA董事会评估该转介（通常要求编制环境影响报告或EIS），并发布对许可具有约束力的环境条件。 - 冷却用水量大时还涉及TasWater服务及Hydro Tasmania水许可问题。 | EPA Tasmania (Board of the EPA) | Environmental Management and Pollution Control Act 1994 (Tas) s 25, Sch 2 (Level 2 activities) | 4–12 months, integrated with permit | FED | No Commonwealth equivalent unless EPBC triggered. | 除触发EPBC外无联邦对应程序。 | https://www.premier.tas.gov.au/latest-news/2026/september/clear-expectations-for-data-centres-and-ai-infrastructure
TAS | 4 | TasNetworks transmission load connection: enquiry, application and 'committed' criteria | TasNetworks输电接入及"已承诺"标准 | TasNetworks runs a standard NER Chapter 5 process but applies its own strict 'committed project' test. - TasNetworks follows the NER Chapter 5 process (enquiry cl 5.3.2–5.3.3, application cl 5.3.4, offer cl 5.3.6), using its Transmission customer connection enquiry form and Guide to Applying for a Transmission Connection. - Because the NER does not define when a load is 'committed', TasNetworks only treats a project as committed once it has firm land rights, a complete connection application, selected major plant suppliers, all planning consents, progressed performance standards, Board approvals from both sides with an executed Asset Development Agreement and Customer Connection Agreement, and written confirmation of financial close. - Available 110/220 kV capacity is concentrated in the north (George Town/Bell Bay) and around Hobart; Marinus Link and the North West Transmission Developments will change headroom from 2028–30. | TasNetworks遵循标准的NER第5章程序，但自设了严格的“已承诺项目”标准。 - TasNetworks遵循NER第5章接入程序（咨询第5.3.2–5.3.3条、申请第5.3.4条、报价第5.3.6条），使用其输电客户接入咨询表及《输电接入申请指南》。 - 由于NER未定义负荷何时“已承诺”，TasNetworks仅在项目具备确定土地权利、完整接入申请、已选定主要设备供应商、取得全部规划许可、性能标准已推进、双方董事会批准并签署资产开发协议和客户接入协议、以及融资关闭书面确认后，才视为已承诺。 - 可用110/220 kV容量集中在北部（George Town/Bell Bay）及霍巴特周边；Marinus Link和西北输电开发项目将在2028–30年改变裕度。 | TasNetworks (TNSP); AEMO (advisory matters) | NER cl 5.3.2–5.3.7, Schedule 5.3; Electricity Supply Industry Act 1995 (Tas) network licence conditions; TasNetworks Transmission Load Connections Process | Enquiry 30–40 business days; 18–30 months enquiry to energisation | FED | Pure NER process; TasNetworks' committed-project criteria are contractual policy and echo Transgrid's readiness tests. | 纯NER程序；TasNetworks的已承诺项目标准属合同政策，与Transgrid的准备度测试类似。 | https://www.tasnetworks.com.au/connections/connections-content/transmission-connections/transmission-load-connections-process ¦ https://www.tasnetworks.com.au/Documents/Manual-documents/Transmission/Guide-to-Transmission-Connections
TAS | 5 | Distribution connection (TasNetworks as DNSP) for smaller loads | 配电接入（TasNetworks作DNSP） | Smaller loads connect under NER Chapter 5A, with TasNetworks' dual TNSP/DNSP role easing any later upgrade. - Loads below roughly 20–30 MW connect at 11/22/33 kV under NER Chapter 5A Part D (negotiated connection, offer within 65 business days of a complete application), with capital contributions under TasNetworks' AER-approved connection policy. - TasNetworks' connections hub routes customers by connection type. - Because the same organisation handles transmission, an upgrade from distribution to transmission connection as a campus grows is coordinated internally. | 较小负荷依NER第5A章接入，TasNetworks兼任TNSP/DNSP便于后续升级。 - 约20–30 MW以下负荷依NER第5A章D部分（协商接入，完整申请后65个工作日内报价）以11/22/33 kV接入，并按TasNetworks经AER批准的接入政策缴纳资本分摊。 - TasNetworks接入中心按接入类型对客户分流。 - 由于同一机构负责输电，园区扩张时从配电升级为输电接入可在内部协调完成。 | TasNetworks (DNSP); AER | NER Chapter 5A Parts D–E; TasNetworks Connection Policy (AER 2024–29) | Offer 65 business days; 6–12 months total | FED | Pure NER process. | 纯NER程序。 | https://www.tasnetworks.com.au/connections/connections-hub/what-type-of-connection-do-you-require
TAS | 6 | Connection agreements, augmentation and cost sharing; renewable generation support expectation | 接入协议、扩建与成本分担 | Cost sharing follows NER mechanics, but Tasmania's small customer base makes socialised augmentation costs politically sensitive. - Connection assets are funded by the customer under the Customer Connection Agreement/Asset Development Agreement. - Shared augmentation is subject to the RIT-T (cl 5.16) and regulated recovery, which is politically sensitive given Tasmania's small customer base. - The Draft Expectations accordingly require proponents to 'meet their share of network and connection costs' and 'support additional renewable energy generation'; reported Government policy also requires major data centre loads to be matched by new renewable generation to protect grid security. - Hydro Tasmania's contracting capacity and Marinus Link timing constrain how much firm renewable supply can be offered. | 成本分担遵循NER机制，但塔州用户基数小，使增容成本社会化分摊在政治上较为敏感。 - 接入资产由客户依客户接入协议/资产开发协议出资。 - 共享扩建须经RIT-T（第5.16条）并由受监管收入回收，鉴于塔州用户基数小，这在政治上较为敏感。 - 《期望草案》因此要求业主“承担其应分摊的网络及接入成本”并“支持新增可再生发电”；据报道州政府政策还要求重大数据中心负荷须配套新建可再生发电以保护电网安全。 - Hydro Tasmania的合约供应能力及Marinus Link时间表限制了可提供的可靠可再生电力规模。 | TasNetworks; AER; Tasmanian Government (Expectations) | NER cl 5.3.7, 5.16 RIT-T, Chapter 6A Part D; Draft Expectations (Sept 2026) | 6–12 months to executed agreements | FED | National cost-allocation rules apply; Tasmania's Expectations anticipate the Commonwealth 'pay full network costs' and 'underwrite new supply' standards. | 适用全国成本分担规则；塔州期望框架预先呼应了联邦“全额支付网络成本”及“承保新增供电”标准。 | https://www.premier.tas.gov.au/latest-news/2026/september/clear-expectations-for-data-centres-and-ai-infrastructure ¦ https://www.examiner.com.au/story/9346904/secret-tassie-ai-data-centre-plans-exposed-in-new-document/
TAS | 7 | Retailer/FRMP, AEMO registration, metering, commissioning and energisation | 零售商/FRMP、注册、调试与送电 | Retail contracting, registration, metering and commissioning follow the standard national process. - Supply is contracted from Aurora Energy or a contestable retailer (customers above 150 MWh/yr are contestable, with the Tasmanian Economic Regulator overseeing retail), or the operator registers as a Market Customer. - Metering follows NER Chapter 7. - TasNetworks witnesses commissioning under NER cl 5.7–5.8, and electrical installations require certificates under the Occupational Licensing Act 2005. - Staged energisation aligned with generation contracting is expected given the Government's new-generation policy. | 零售合约、注册、计量与调试遵循全国标准程序。 - 电力从Aurora Energy或可竞争零售商购买（年用电量超过150 MWh的客户可自由选择，塔州经济监管官监督零售），或运营商注册为市场客户。 - 计量遵循NER第7章。 - TasNetworks依NER第5.7–5.8条见证调试，电气装置须依《2005年职业许可法》取得证书。 - 鉴于州政府的新建电源政策，预计送电将与发电合约进度分阶段匹配。 | Retailer/FRMP; AEMO; TasNetworks; Office of the Tasmanian Economic Regulator | NER Chapters 2, 5 (cl 5.7–5.8) and 7; Electricity Supply Industry Act 1995 (Tas); Occupational Licensing Act 2005 (Tas) | 3–9 months retail; commissioning 2–6 months per stage | FED | National process; Tasmania adds electrical licensing sign-off only. | 全国程序；塔州仅增加电气许可签核。 | https://www.tasnetworks.com.au/connections/connections-content/transmission-connections/transmission-load-connections-process
ACT | 1 | Site selection under the Territory Plan and forthcoming ACT Data Centre Framework locations | 选址：领地规划及框架优先走廊 | Siting turns on Crown lease purpose clauses and the Framework's forthcoming preferred corridors. - Land in the ACT is leasehold; the Crown lease purpose clause must permit the use (data centres typically fall within 'industry' or 'communications facility' uses in IZ1/IZ2 industrial zones at Hume, Fyshwick, Majura and Symonston, or CZ commercial zones), otherwise a lease variation is needed alongside the development application. - The August 2026 Framework confirms data centres will be limited to zones already permitting them, with Government to identify preferred corridors combining industrial zoning, transport links and utility capacity (draft due early 2027). - The Suburban Land Agency and CMTEDD's investment team facilitate site releases. - Icon Water and Evoenergy are consulted on servicing at this stage. | 选址取决于皇家租约用途条款及框架即将确定的优先走廊。 - 首都领地土地为租赁制；皇家租约用途条款须允许该用途（数据中心通常属于Hume、Fyshwick、Majura及Symonston等IZ1/IZ2工业区的“工业”或“通信设施”用途，或CZ商业区），否则须在开发申请的同时变更租约。 - 2026年8月框架确认数据中心仅限于现行允许的分区，政府将确定兼具工业分区、交通连接及公用设施容量的优先走廊（草案预计2027年初发布）。 - 郊区土地局及CMTEDD投资团队协助土地释放。 - 此阶段征询Icon Water及Evoenergy对供水供电的意见。 | Territory Planning Authority; Suburban Land Agency; CMTEDD | Planning Act 2023 (ACT); Territory Plan 2023 (zone development tables); Planning (General) Regulation 2023; Crown lease purpose clauses | 2–6 months (longer with lease variation) | FED | Commonwealth land (National Capital Plan areas administered by the National Capital Authority) is subject to Commonwealth works approval instead of ACT planning; FIRB applies to foreign proponents. | 联邦土地（由国家首都管理局管理的国家首都规划区域）适用联邦工程批准而非首都领地规划；FIRB适用于外国业主。 | https://www.cmtedd.act.gov.au/open_government/inform/act_government_media_releases/barr/2026/providing-a-clear-framework-for-data-centres-in-the-act ¦ https://www.abc.net.au/news/2026-08-23/act-data-centre-policy-already-aligned-with-national-ai-standard/106936530
ACT | 2 | Development approval under the Planning Act 2023 (merit/impact track, Territory Priority Project option) | 开发批准（评审/影响轨道，领地优先项目） | Development approval runs through a merit or impact track, with a ministerial fast-track available. - A development application is lodged with the Territory Planning Authority and assessed against the Territory Plan's outcomes-focused district and zone policies. - Most data centres are 'merit track' (public notification, referrals to Evoenergy, Icon Water, EPA and TCCS; decision within 30–45 working days after notification); proposals requiring an EIS under Schedule 1 of the Planning Act are 'impact track'. - The Minister may declare a Territory Priority Project, removing third-party ACAT review, or call in a DA. - The 2026 Framework foreshadows sustainability and infrastructure assessment criteria being embedded in the Territory Plan through a technical specification or variation in 2027. | 开发批准走评审或影响轨道，部长可启用快速通道。 - 开发申请向领地规划局提交，按《领地规划》以结果为导向的地区及分区政策评估。 - 多数数据中心属“评审轨道”（公告、转介Evoenergy、Icon Water、EPA及TCCS；公告后30–45个工作日内决定）；依《规划法》附表1需编制EIS的提案属“影响轨道”。 - 部长可宣布领地优先项目以取消第三方ACAT复审，或召回开发申请。 - 2026年框架预示可持续性及基础设施评估标准将于2027年通过技术规范或变更纳入《领地规划》。 | Territory Planning Authority; Minister for Planning (Territory Priority Projects, call-in); ACAT (review) | Planning Act 2023 (ACT) ch 6 (development assessment), s 196 (Territory Priority Projects), Sch 1 (EIS triggers); Territory Plan 2023 | Merit track 3–6 months; impact track 12–18 months | FED | EPBC applies to Commonwealth-significant matters and the ACT–Commonwealth bilateral assessment agreement; National Cabinet standards will overlay in 2027. | EPBC适用于联邦重要事项及首都领地–联邦双边评估协议；国家内阁标准将于2027年叠加。 | https://www.cmtedd.act.gov.au/open_government/inform/act_government_media_releases/barr/2026/providing-a-clear-framework-for-data-centres-in-the-act
ACT | 3 | Environmental authorisation (ACT EPA) and Icon Water servicing | 环境授权（首都领地EPA）及Icon Water供水 | Environmental authorisation and water servicing run alongside the development application. - Under the Environment Protection Act 1997, Schedule 1 activities (including electricity generation above set thresholds and bulk fuel storage) require an environmental authorisation from the ACT EPA, and noise limits apply under the Environment Protection Regulation. - The Framework requires best-practice water efficiency and minimal impact on water and wastewater infrastructure. - Icon Water servicing agreements, including developer charges, are required, and cooling-water demand is a referral consideration. | 环境授权及供水服务与开发申请同步办理。 - 依《1997年环境保护法》，附表1所列活动（包括超过规定门槛的发电及大宗燃油储存）需向首都领地EPA申领环境授权，噪声限值依《环境保护条例》适用。 - 框架要求最佳实践用水效率并尽量减少对供水及污水基础设施的影响。 - 须与Icon Water签订服务协议（含开发商费用），冷却用水需求是转介审查的考量因素。 | ACT EPA (Access Canberra); Icon Water | Environment Protection Act 1997 (ACT) s 42 and Sch 1; Utilities Act 2000 (ACT) (Icon Water and Evoenergy licences) | 2–6 months, concurrent with DA | FED | No Commonwealth equivalent unless EPBC triggered. | 除触发EPBC外无联邦对应程序。 | https://www.cmtedd.act.gov.au/open_government/inform/act_government_media_releases/barr/2026/providing-a-clear-framework-for-data-centres-in-the-act
ACT | 4 | Evoenergy connection enquiry and application (NER Chapter 5A / 5) and Transgrid supply-point capacity | Evoenergy接入及Transgrid供电点容量 | Distribution connection is straightforward via Evoenergy, but larger loads pull in Transgrid's NSW capacity regime. - Evoenergy is the sole DNSP; large loads connect at 11 kV or 132 kV from its zone substations under the NER Chapter 5A negotiated-connection process (offer within 65 business days of a complete application), or Chapter 5 for the largest sites. - The ACT is supplied by Transgrid's 330 kV Canberra and Williamsdale substations and 132 kV lines, so campuses above roughly 50–100 MW, or clusters in Hume/Symonston, can require Transgrid augmentation in NSW under NER Chapter 5. - That brings ACT loads within Transgrid's Network Capacity Allocation Policy for ≥30 MW inverter-based loads and the NSW large-load reforms. - Evoenergy's network projects page lists augmentation works, and it publishes capacity through its Distribution Annual Planning Report. | 配电接入通过Evoenergy办理较为直接，但较大负荷会牵涉Transgrid的新州容量制度。 - Evoenergy是唯一的配电商；大负荷从其区域变电站以11 kV或132 kV接入，适用NER第5A章协商接入程序（完整申请后65个工作日内报价），或对最大型场址适用第5章。 - 首都领地由Transgrid的330 kV堪培拉及Williamsdale变电站及132 kV线路供电，因此约50–100 MW以上的园区或Hume/Symonston的集群可能需要Transgrid依NER第5章在新州境内扩建。 - 这使首都领地负荷落入Transgrid针对30 MW及以上逆变器型负荷的《网络容量分配政策》及新州大负荷改革范围。 - Evoenergy网络项目页面列出扩建工程，并通过《配电年度规划报告》公布容量。 | Evoenergy (DNSP); Transgrid (TNSP) for upstream capacity; AEMO (advisory matters) | NER Chapter 5A Part D; NER cl 5.3.2–5.3.7 (Chapter 5) where applicable; Utilities Act 2000 (ACT) distribution licence; Evoenergy Connection Policy (AER 2024–29) | Offer 65 business days (Ch 5A) or 4 months (Ch 5); 12–24 months where Transgrid works needed | FED, NSW | Upstream capacity is governed by Transgrid in NSW, so the ACT proponent may face both NER Chapter 5 with Transgrid and any NSW EII Act access-scheme terms even though the site is in the ACT. | 上游容量由新州境内的Transgrid管理，即便场址位于首都领地，业主也可能同时面对与Transgrid的NER第5章程序及新州《电力基础设施投资法》接入计划条款。 | https://www.evoenergy.com.au/Future-energy/Network-projects ¦ https://www.transgrid.com.au/about-us/network/network-connections/data-centres-and-electricity-capacity-in-nsw/
ACT | 5 | Connection offer, agreement and cost allocation | 接入报价、协议与成本分担 | Cost allocation follows Evoenergy's standard NER mechanics, with any Transgrid works priced separately. - Evoenergy issues a negotiated connection offer and connection contract; connection assets and load-driven zone-substation augmentation are customer-funded capital contributions under its AER-approved connection policy. - Shared augmentation must pass the RIT-D (cl 5.17) and is recovered through Evoenergy's regulated revenue (the ICRC no longer sets network prices but regulates retail). - Any Transgrid works in NSW are priced as negotiated transmission services. - The ACT has not proposed NSW-style bonds or upgrade fees; the pending Commonwealth cost-recovery rules would apply instead. | 成本分担遵循Evoenergy标准的NER机制，Transgrid工程另行计价。 - Evoenergy发出协商接入报价并签订接入合同；接入资产及由负荷引起的区域变电站扩建依其经AER批准的接入政策由客户以资本分摊出资。 - 共享扩建须通过RIT-D（第5.17条）并通过Evoenergy受监管收入回收（ICRC不再制定网络价格，但监管零售）。 - Transgrid在新州境内的工程按协商输电服务定价。 - 首都领地未提议新州式保证金或升级费；待审的联邦成本回收规则将替代适用。 | Evoenergy; Transgrid; AER | NER Chapter 5A Part E (connection charges), cl 5.17 RIT-D, cl 5.3.6–5.3.7, Chapter 6A Part D | 6–12 months to executed agreement | FED, NSW | National NER cost allocation applies; NSW state fees could attach to any Transgrid connection point used to serve the ACT site. | 适用全国NER成本分担；新州州级费用可能附加于用于供电首都领地场址的任何Transgrid接入点。 | https://www.evoenergy.com.au/Future-energy/Network-projects
ACT | 6 | Renewable offset requirement, retailer/FRMP and AEMO registration | 可再生抵消要求、FRMP与AEMO注册 | The renewable offset requirement pre-empts the coming national standard. - The ACT already sources 100% renewable electricity for territory consumption through large-scale feed-in-tariff contracts under the Electricity Feed-in (Large-scale Renewable Energy Generation) Act 2011. - The August 2026 Framework requires new data centres to offset additional demand through investment in new renewable generation, so they 'help build new renewable energy, not simply consume existing capacity'; the mechanism (PPA, REGO surrender or contribution) will be set out in the 2027 draft. - A retailer licensed by the ICRC is appointed as FRMP, or the operator registers with AEMO. - The ACT Government has told the ABC its policy already aligns with the national standard. | 可再生抵消要求已先行呼应即将出台的全国标准。 - 首都领地已依《2011年电力上网（大规模可再生能源发电）法》通过大规模上网电价合约实现领地用电100%可再生。 - 2026年8月框架要求新建数据中心通过投资新建可再生发电抵消其新增需求，使其“帮助建设新的可再生能源，而非仅消耗现有容量”；具体机制（PPA、REGO注销或出资）将在2027年草案中明确。 - 指定持有ICRC牌照的零售商为FRMP，或运营商向AEMO注册。 - 首都领地政府已向ABC表示其政策已与全国标准一致。 | ACT Government (Framework); retailer/FRMP; AEMO; ICRC | ACT Data Centre Framework (announced 26 Aug 2026, draft due early 2027); Electricity Feed-in (Large-scale Renewable Energy Generation) Act 2011 (ACT); Climate Change and Greenhouse Gas Reduction Act 2010 (ACT); NER Chapter 2 | PPA/REGO procurement 6–18 months | FED | The ACT requirement pre-empts and aligns with the Commonwealth REGO/new-generation standard; a single PPA can be structured to satisfy both. | 首都领地的要求先于并契合联邦REGO/新建电源标准；可通过单一PPA同时满足两者。 | https://www.cmtedd.act.gov.au/open_government/inform/act_government_media_releases/barr/2026/providing-a-clear-framework-for-data-centres-in-the-act ¦ https://www.abc.net.au/news/2026-08-23/act-data-centre-policy-already-aligned-with-national-ai-standard/106936530
ACT | 7 | Metering, commissioning, energisation and Hosting Certification for government tenants | 计量、调试、送电与托管认证 | Energisation combines standard NER metering/commissioning with federal certification for government tenants. - Metering follows NER Chapter 7; Access Canberra electrical inspectors certify installations under the Electricity Safety Act 1971 before Evoenergy energises the connection and witnesses commissioning (NER cl 5.7–5.8). - Because the Canberra market is dominated by Commonwealth tenants, operators typically also pursue Hosting Certification Framework 'Certified Strategic' status through Home Affairs. - SOCI Act registration is also typically pursued. - Both the Hosting Certification and SOCI processes are federal and independent of the grid connection. | 送电环节结合标准的NER计量/调试与面向政府租户的联邦认证。 - 计量遵循NER第7章；Access Canberra电气检查员依《1971年电力安全法》认证装置后，Evoenergy送电并见证调试（NER第5.7–5.8条）。 - 由于堪培拉市场以联邦租户为主，运营商通常还通过内政部申请托管认证框架“认证战略级”资格。 - 通常还一并办理SOCI法登记。 - 托管认证及SOCI两项程序均属联邦事项，独立于并网程序。 | Evoenergy; Access Canberra; Department of Home Affairs (Hosting Certification, SOCI) | NER cl 5.7–5.8, Chapter 7; Electricity Safety Act 1971 (ACT); Hosting Certification Framework; SOCI Act 2018 (Cth) | Commissioning 2–6 months; Hosting Certification 6–12 months | FED | Hosting Certification and SOCI are purely federal; the ACT adds only electrical safety sign-off. | 托管认证和SOCI纯属联邦事项；首都领地仅增加电气安全签核。 | https://www.hostingcertification.gov.au/ ¦ https://www.cisc.gov.au/information-for-your-industry/data-storage-and-processing/legislation-regulation-and-compliance/soci-act-2018
NT | 1 | Site selection, Crown land deals and Territory Coordinator engagement | 选址、皇家土地安排及领地协调官对接 | Most projects start with a Crown land deal, then Territory Coordinator engagement. - Most large sites are Crown land released by the NT Government (e.g. 185 ha at Weddell granted to Beetaloo Digital with 12-month exclusivity in July 2026, and land in the Middle Arm Sustainable Development Precinct), so the first step is a land agreement with the Department of Logistics and Infrastructure/Land Development Corporation. - The Territory Coordinator (Territory Coordinator Act 2025) can declare a 'significant project' to coordinate, and where authorised, modify statutory approvals. - Native title (Larrakia and other groups) and Aboriginal Areas Protection Authority certificates are needed for greenfield land. | 多数项目先办理皇家土地安排，再对接领地协调官。 - 多数大型场址为北领地政府释放的皇家土地（如2026年7月授予Beetaloo Digital的Weddell 185公顷土地并附12个月独家权，以及Middle Arm可持续发展区土地），因此第一步是与物流与基础设施部/土地开发公司签订土地协议。 - 领地协调官（《2025年领地协调官法》）可宣布“重大项目”以协调，并在获授权时修改法定审批。 - 新开发土地需办理原住民土地权（Larrakia等群体）及原住民地区保护局证书。 | NT Government (land); Territory Coordinator; Aboriginal Areas Protection Authority | Crown Lands Act 1992 (NT); Territory Coordinator Act 2025 (NT); Northern Territory Aboriginal Sacred Sites Act 1989 | 3–12 months | FED | FIRB applies to foreign proponents; Commonwealth Native Title Act 1993 processes run alongside NT land dealings. | FIRB适用于外国业主；联邦《1993年原住民土地权法》程序与北领地土地交易并行。 | https://ntindependent.com.au/nt-government-backs-proposed-2gw-data-centre-at-weddell/ ¦ https://www.abc.net.au/news/2026-07-22/beetaloo-digital-energy-ai-hyperscale-data-centre-40-billion/106943690
NT | 2 | Development permit under the Planning Act 1999 / NT Planning Scheme 2020 | 开发许可（规划法/北领地规划方案） | Development approval follows the standard Planning Act process, with rezoning often needed for greenfield sites. - A development application is lodged with Development Assessment Services and determined by the Development Consent Authority (or the Minister for significant/called-in matters) under Part 5 of the Planning Act 1999, assessed against NT Planning Scheme 2020 zone tables (data centres fit 'industry'/'general industry' zones such as GI/LI at East Arm, Berrimah or the proposed Weddell precinct). - Public exhibition and referral to Power and Water and the NT EPA apply; the statutory decision period is 84 days after exhibition. - Rezoning (a Planning Scheme amendment by the Minister) is often needed for greenfield precincts, adding 6–12 months. - Under the Territory Coordinator Act, the Coordinator can issue step-in or exemption notices to accelerate significant projects. | 开发批准遵循标准的规划法程序，新开发场址常需先重新分区。 - 开发申请向开发评估服务处提交，依《1999年规划法》第5部分由开发许可局（重大或召回事项由规划部长）裁定，按《2020年北领地规划方案》分区表评估（数据中心适合East Arm、Berrimah或拟建Weddell园区等GI/LI“工业”/“一般工业”区）。 - 须公示并转介Power and Water及北领地EPA；公示后法定决定期为84天。 - 新开发园区常需重新分区（由部长修订规划方案），额外增加6–12个月。 - 依《领地协调官法》，协调官可发出介入或豁免通知以加快重大项目审批。 | Development Consent Authority / Minister for Planning; Territory Coordinator | Planning Act 1999 (NT) Part 5 (development applications), Part 2 (scheme amendments); NT Planning Scheme 2020; Territory Coordinator Act 2025 | 4–9 months; 12–18 months with rezoning | FED | EPBC referral is common for Top End greenfield sites (threatened species, wetlands) and is coordinated with the NT EPA under the bilateral agreement; National Cabinet standards will overlay in 2027. | 北端地区新开发场址常需EPBC评估（受威胁物种、湿地），依双边协议与北领地EPA协调；国家内阁标准将于2027年叠加。 | https://ntindependent.com.au/nt-government-backs-proposed-2gw-data-centre-at-weddell/
NT | 3 | Environmental approval (Environment Protection Act 2019) and on-site generation licensing | 环境批准及现场发电许可 | Environmental approval and generation licensing apply in parallel, especially where on-site gas generation is proposed. - Proposals with potentially significant environmental impact must be referred to the NT EPA under the Environment Protection Act 2019, which decides the assessment tier (referral information, supplementary report, or full EIS); large on-site gas-fired generation, as proposed at Weddell, will almost certainly require an EIS. - The Minister for Environment grants the environmental approval, with conditions. - Generation above licensing thresholds also needs a generation licence from the Utilities Commission under the Electricity Reform Act 2000. - Emissions above 100kt CO2-e per year are subject to the Commonwealth Safeguard Mechanism. | 环境批准及发电许可并行适用，现场燃气发电项目尤其如此。 - 可能产生重大环境影响的提案须依《2019年环境保护法》转介北领地EPA，由EPA决定评估层级（转介资料、补充报告或完整EIS）；大型现场燃气发电（如Weddell拟议方案）几乎必然需要EIS。 - 环境部长附条件批准环境审批。 - 超过许可门槛的发电还需依《2000年电力改革法》向公用事业委员会申领发电许可。 - 年排放超过10万吨CO2当量的还受联邦保障机制约束。 | NT EPA; Minister for Environment; Utilities Commission (licensing) | Environment Protection Act 2019 (NT) Parts 4–5; Electricity Reform Act 2000 (NT) Part 3 (licensing); National Greenhouse and Energy Reporting Act 2007 (Cth) Safeguard Mechanism | EIS 12–24 months; licence 3–6 months | FED | EPBC and Safeguard Mechanism obligations are federal and additional to NT approvals. | EPBC及保障机制义务属联邦层面，叠加于北领地审批之上。 | https://www.abc.net.au/news/2026-07-22/beetaloo-digital-energy-ai-hyperscale-data-centre-40-billion/106943690
NT | 4 | Power and Water major customer connection: enquiry, engagement package, formal application and response | Power and Water大客户接入咨询与申请 | Access follows a four-step major-customer enquiry process specific to Power and Water. - Loads above 2 MW aggregated capacity or 10% of local network capacity, and all 66 kV-and-above connections, use the major customer process: initial enquiry to majorconnections.pwc@powerwater.com.au with site, MW/MVA, consumption profile, technology and timeline. - Power and Water then issues a connection engagement package, and the proponent lodges the Large Connection Enquiry Form with single-line diagram, inverter details, maximum demand and disturbing-load data (an electrical engineer is recommended). - A processing fee is quoted, and on payment a detailed enquiry response is issued within 30 business days. - Technical requirements follow the Network Technical Code and Planning Criteria; Power and Water publishes generic environmental and development approval guidance per NER Schedule 5.10 as modified for the NT. | 接入遵循Power and Water特有的四步大客户咨询流程。 - 合计容量超过2 MW或占当地网络容量10%的负荷，以及所有66 kV及以上接入，均使用大客户程序：向majorconnections.pwc@powerwater.com.au提交初步咨询，说明场址、MW/MVA、用电曲线、技术及时间表。 - Power and Water随后发出接入对接材料包，业主提交《大型接入咨询表》，附单线图、逆变器详情、最大需求及扰动负荷数据（建议由电气工程师完成）。 - 报出处理费，付费后30个工作日内出具详细咨询回复。 - 技术要求遵循《网络技术守则及规划标准》；Power and Water按经北领地修改的NER附表5.10公布通用环境及开发批准指引。 | Power and Water Corporation (network operator) | Electricity Networks (Third Party Access) Act 2000 (NT) and Network Access Code; Network Technical Code and Network Planning Criteria; Power and Water Connection Policy 2024–29 (AER-approved) | Detailed response 30 business days after fee; enquiry phase 2–4 months |  | NEM Chapter 5 processes do not apply; the NT Network Access Code is the local equivalent, and AEMO has no operational role in the NT. | NEM第5章程序不适用；北领地《网络接入守则》是本地对应机制，AEMO在北领地无运营职能。 | https://www.powerwater.com.au/developers/power/major-customer-connections ¦ https://www.powerwater.com.au/development/power/technical-code-and-planning-criteria
NT | 5 | Connection offer, Negotiated Connection and Supply Contract, NTESMO and Utilities Commission approvals | 接入报价、供电合同及NTESMO/公用事业委员会批准 | Finalising the connection requires dual sign-off from NTESMO and the Utilities Commission on top of Power and Water's offer. - Power and Water issues a formal connection offer and a Negotiated Connection and Supply Contract (load facilities template) after network studies. - The connection also requires NTESMO (system operator) approval of the technical arrangements and Utilities Commission approval or non-objection before finalisation; a Major Connections Processing Agreement governs cost recovery for the study work. - Capital contributions for connection assets and augmentation follow the AER-approved Connection Policy 2024–29 (user-pays for dedicated assets; contributions where incremental revenue is insufficient). - Given the system's small size, large loads may be required to fund new generation or firming (Territory Generation or private) or accept interruptibility. | 在Power and Water出具报价之外，最终确定接入还需NTESMO及公用事业委员会双重批准。 - 网络研究完成后，Power and Water发出正式接入报价及《协商接入与供电合同》（负荷设施模板）。 - 接入还需NTESMO（系统运营商）批准技术安排，并经公用事业委员会批准或无异议后方可最终确定；《大型接入处理协议》规范研究工作的成本回收。 - 接入资产及扩建的资本分摊遵循AER批准的《2024–29年接入政策》（专用资产由用户付费；增量收入不足时收取分摊）。 - 鉴于系统规模小，大负荷可能被要求出资新建发电或可靠容量（Territory Generation或私营）或接受可中断供电。 | Power and Water; NTESMO; Utilities Commission of the NT | Electricity Networks (Third Party Access) Act 2000 (NT); Network Access Code; Electricity Reform Act 2000 (NT); System Control Technical Code; Power and Water Connection Policy 2024–29 | 6–12 months to executed contract |  | Purely NT-regulated; the AER's role is limited to Power and Water's revenue determination. | 完全由北领地监管；AER的职能仅限于Power and Water的收入裁定。 | https://www.powerwater.com.au/developers/power/major-customer-connections ¦ https://www.powerwater.com.au/__data/assets/pdf_file/0026/354383/Major-connections-processing-agreement-template.pdf ¦ https://www.aer.gov.au/system/files/PWC%20-%208.62%20-%20Connection%20Policy%20-%2031%20Jan%2023%20-%20Public.pdf
NT | 6 | Energy supply: retailer licence, I-NTEM participation or self-generation (energy-agnostic) | 能源供应：零售、I-NTEM或自发电 | Given the system's limited absorption capacity, hyperscale demand is met mainly by on-site generation rather than the grid. - Electricity is bought from Jacana Energy or another Utilities Commission-licensed retailer (contestable above 750 MWh/yr), which procures from Territory Generation or independent generators under the I-NTEM operated by NTESMO; there is no NEM-style spot market registration. - Because the Darwin–Katherine system cannot absorb hundreds of megawatts, hyperscale proponents such as Beetaloo Digital plan on-site gas-fired generation (up to 2 GW from Beetaloo Basin gas), with grid connection used for backup or export. - The generator itself needs generation licences and NTESMO connection approval. - The NT, with Queensland, obtained an energy-agnostic firming approach in the National Cabinet framework, though REGO-based renewable offsets will still apply once Commonwealth legislation passes. - In its 25 September 2026 submission the NT Government opposed any mandatory requirement to fully offset data centre demand with new renewable generation, arguing for dedicated standalone generation outside the regulated system and outcomes-based, technology-neutral national standards. | 由于系统吸纳能力有限，超大规模需求主要靠现场发电而非电网满足。 - 电力从Jacana Energy或其他持有公用事业委员会牌照的零售商购买（年用电量超过750 MWh可自由选择），零售商依NTESMO运营的I-NTEM从Territory Generation或独立发电商采购；不存在NEM式的现货市场注册。 - 由于达尔文–凯瑟琳系统无法吸纳数百兆瓦负荷，Beetaloo Digital等超大规模业主计划现场燃气发电（利用Beetaloo盆地天然气最多2 GW），电网仅用于备用或外送。 - 发电机本身也需取得发电许可及NTESMO接入批准。 - 北领地与昆州在国家内阁框架中争取到能源技术中立的可靠容量方式，但联邦立法通过后基于REGO的可再生抵消仍将适用。 - 北领地政府在2026年9月25日的意见中反对强制以新建可再生发电全额抵消数据中心用电，主张采用独立于受监管系统之外的专用电源，并要求全国标准以结果为导向、技术中立。 | Utilities Commission (licensing); NTESMO (I-NTEM); retailers | Electricity Reform Act 2000 (NT); Electricity Reform (Administration) Regulations; I-NTEM Rules (NTESMO); National Cabinet framework (26 Aug 2026) | Retail 3–6 months; self-generation development 24–36 months | FED | Commonwealth REGO and firm-capacity standards will need NT-specific implementation since AEMO registration is not available in the NT. | 由于北领地无法向AEMO注册，联邦REGO及可靠容量标准须在北领地另行落实。 | https://www.abc.net.au/news/2026-07-22/beetaloo-digital-energy-ai-hyperscale-data-centre-40-billion/106943690 ¦ https://www.claytonutz.com/insights/2026/august/nine-governments-one-rulebook-national-cabinet-backs-mandatory-ai-and-data-centre-standards
NT | 7 | Metering, commissioning witness and energisation | 计量、调试见证与送电 | Final commissioning combines metering, technical witnessing and safety inspection before full capacity is released. - Power and Water installs revenue metering under the NT Electricity Metering Code and witnesses final commissioning against the Network Technical Code. - Post-commissioning documentation is required before full capacity is released. - Installations must be certified under the Electricity Reform (Safety and Technical) Regulations by a licensed electrical contractor and inspected by NT WorkSafe. - Staged energisation is likely given the small size of the Top End system. | 最终调试结合计量安装、技术见证及安全检查，全部容量方可释放。 - Power and Water依《北领地电力计量守则》安装结算计量装置，并按《网络技术守则》见证最终调试。 - 释放全部容量前须提交调试后文件。 - 装置须由持证电气承包商依《电力改革（安全与技术）条例》认证，并经NT WorkSafe检查。 - 鉴于北端系统规模较小，送电很可能分阶段进行。 | Power and Water; NT WorkSafe; NTESMO | NT Electricity Metering Code (Utilities Commission); Network Technical Code; Electricity Reform (Safety and Technical) Regulations 2000 | Commissioning 2–6 months per stage |  | Purely NT-regulated; no NER Chapter 7 metering rules. | 完全由北领地监管；不适用NER第7章计量规则。 | https://www.powerwater.com.au/developers/power/major-customer-connections

## Reg_Changes
jurisdiction_id | date | summary_en | summary_zh | source
FED | 2026-03 | AEMC published the draft determination for 'Improving the NEM access standards – Package 2' (ERC0394), lifting the large inverter-based load threshold from 5 MW to 30 MW and adding ride-through and instability-detection standards; final determination now due 29 October 2026. The Commonwealth also released its Expectations of Data Centres and AI Infrastructure Developers (23 March). | 8月5日AEMC向部长建议：数据中心须注销新建电源的REGO证书、签订新增可靠容量合约、向AEMO注册并提供需求灵活性；8月26日国家内阁通过覆盖能源、水及土地利用的全国强制性数据中心标准，联邦立法预计2027年初，昆州/北领地争取到能源技术中立的可靠容量方式。 | https://www.aemc.gov.au/rule-changes/improving-nem-access-standards-package-2
FED | 2026-07 | AEMO lodged ERC0455 (operational integration and visibility of large inverter-based loads, 21 July) and Minister Bowen lodged two cost-recovery rule changes (ERC0448 Package 1 and Package 2, 22 July) requiring data centres to pay for augmentation, post prudential support and be kept out of regulated asset bases; both pending initiation. EPBC reforms and NEPA commenced 1 July. | 7月21日AEMO提交ERC0455（大型逆变器型负荷运行整合与可见性）；7月22日Bowen部长提交两项成本回收规则修改（ERC0448第一批及第二批），要求数据中心承担增容费用、提供审慎担保且不计入受监管资产基础，均待AEMC启动；EPBC改革及NEPA于7月1日生效。 | https://www.ashurstperkinscoie.com/en/insights/australian-electricity-and-gas-markets-july-2026-update/
FED | 2026-08 | AEMC advice to Ministers (5 August): data centres to surrender REGOs from new generation, contract new firm capacity, register with AEMO and be flexible. National Cabinet (26 August) endorsed mandatory national data centre standards on energy, water and land use, with Commonwealth legislation expected early 2027; Queensland/NT obtained an energy-agnostic firming approach. | 5月19日财政部宣布FIRB改革并将立法落实：2027年1月1日起低风险案件30天内决定，非敏感行业门槛上调，数据中心投资明确对照全国数据中心期望框架评估。 | https://www.claytonutz.com/insights/2026/august/nine-governments-one-rulebook-national-cabinet-backs-mandatory-ai-and-data-centre-standards
FED | 2026-05 | Treasury announced FIRB reforms (19 May) to be enacted by legislation: 30-day decisions for low-risk cases from 1 January 2027, higher thresholds for non-sensitive sectors, and explicit assessment of data centre investments against the national data centre expectations. | AEMC发布Improving the NEM access standards – Package 2（ERC0394）裁定草案，大型逆变器型负荷门槛由5 MW提至30 MW并新增穿越及失稳检测标准，最终裁定改为2026年10月29日；联邦另于3月23日发布数据中心及AI基础设施开发商期望。 | https://www.allens.com.au/insights-news/insights/2026/05/extensive-reforms-to-the-firb-regime/
NSW | 2026-03 | NSW released a data centre consultation paper setting five principles (developer-funded infrastructure, no household price impact, efficient energy/water use, transparent data, size/location-sensitive regulation) and commissioned IPART on water pricing. | 8月5日Electricity Infrastructure Investment Amendment Bill 2026提交议会，为5 MW及以上负荷设立大负荷接入计划并授权偏离NER；配套咨询文件对15 MW及以上数据中心提出入门保证金、Major Network Upgrade Fee、照付不议及需求响应条款，意见征集于2026年9月14日截止。 | https://www.ashurstperkinscoie.com/en/insights/australia-evolving-data-centre-landscape-policy-meets-pipeline/
NSW | 2026-08 | Electricity Infrastructure Investment Amendment Bill 2026 introduced (5 Aug) creating large load access schemes for ≥5 MW loads and NER derogation powers; consultation paper proposes entry bond, Major Network Upgrade Fee, take-or-pay and demand-response terms for ≥15 MW data centres (submissions closed 14 Sept 2026). | 8月14日Transgrid Network Capacity Allocation Policy生效，适用于30 MW及以上逆变器型负荷：签署NCA才分配容量，三个月内完成六项准备度测试；Transgrid称悉尼盆地容量基本耗尽。 | https://www.mallesons.com/au/en/insights/latest-thinking/another-big-day-for-data-centres-in-nsw-a-new-framework-for-connection.html
NSW | 2026-08 | Transgrid's Network Capacity Allocation Policy took effect (14 Aug) for ≥30 MW inverter-based loads: capacity only on NCA signature, six readiness tests within three months; Sydney basin capacity described as largely exhausted. | 8月17日NSW Data Centre Policy Framework及Guidelines发布：保留SSD路径，SEARs两个月出具，75天审批目标，设PUE/WUE上限、100%再生水、25%/2小时需求灵活性，以及含40%风电与4小时储能的10年期PPA。 | https://w.media/transgrid-sets-six-tests-for-data-centres-seeking-nsw-grid-capacity/
NSW | 2026-08 | NSW Data Centre Policy Framework and Guidelines released (17 Aug): SSD retained, SEARs in 2 months, 75-day assessment target, PUE/WUE limits, 100% recycled water, 25%/2-hour demand flexibility, 10-year PPAs with 40% wind and 4-hour storage. | 新州发布数据中心咨询文件，确立五项原则——开发商出资建设基础设施、不影响居民电价、高效用能用水、数据透明、按规模与区位差异化监管——并委托IPART研究数据中心水价。 | https://www.claytonutz.com/insights/2026/august/nsw-draws-the-line-what-the-new-data-centre-policy-framework-means-for-investors-developers-government-and-communities
VIC | 2026-02 | Victoria released its AI Mission Statement and $5.5 m Sustainable Data Centre Action Plan (25 Feb 2026) with five focus areas: coordinated land/energy/water/transport infrastructure, energy innovation and grid readiness, water security, workforce, and leadership/coordination. | Hume City Council通过动议要求暂停新建数据中心，显示墨尔本北部地方阻力上升；与此同时，2026年多项数据中心部长许可仍经Development Facilitation Program发出。 | https://djsir.vic.gov.au/priorities-and-initiatives/ai-mission-statement/sustainable-data-centre-action-plan
VIC | 2026-08 | Hume City Council passed a motion seeking a moratorium on new data centres, reflecting growing local pushback in Melbourne's north; several 2026 ministerial permits for data centres continued to be issued under the Development Facilitation Program. | 维州于2026年8月26日加入国家内阁强制性数据中心标准；联邦立法2027年通过后，该标准将叠加于P&E Act许可程序之上。 | https://datacentres.civicinterplay.io/sheets/vic
VIC | 2026-08 | Victoria signed on to National Cabinet's mandatory data centre standards (26 Aug 2026) which will overlay the P&E Act permit process once Commonwealth legislation passes in 2027. | VicGrid上线输电接入流程页面及社区参与指引，并预告新的Victorian Access Regime拟2027年生效，过渡期适用临时安排。 | https://www.claytonutz.com/insights/2026/august/nine-governments-one-rulebook-national-cabinet-backs-mandatory-ai-and-data-centre-standards
VIC | 2026-06 | VicGrid published its transmission connections process pages and community engagement guidelines, noting a new Victorian Access Regime due to take effect in 2027 with transitional arrangements. | 维州2026年2月25日发布AI Mission Statement及550万澳元Sustainable Data Centre Action Plan，确定五大重点：土地/能源/水/交通基础设施统筹、能源创新与电网准备度、水安全、劳动力、领导与协调。 | https://www.vicgrid.com.au/industry/access-and-connections/transmission-connections-process
QLD | 2026-01 | Energy Queensland's Large Customer Connection Manual took effect (5 Jan 2026), consolidating Energex/Ergon Chapter 5 and 5A processes, timeframes and cost-recovery categories for large loads. | Zerra DC向Western Downs Regional Council提交达尔比附近2.16 GW的Western Downs Digital Park申请（319亿澳元），拟直连Powerlink变电站并采用燃气/可再生混合供电，是昆州议会DA路径承接超大规模负荷的最大考验。 | https://www.energex.com.au/__data/assets/pdf_file/0011/1090649/Large-Customer-Connection-Manual-3040635.pdf
QLD | 2026-08 | Premier Crisafulli opposed renewable-only sourcing, secured an energy-agnostic firming approach at National Cabinet (26 Aug), and announced data centres will need a social impact assessment and community benefit agreement with councils before lodging a DA. | 州长Crisafulli反对仅限可再生能源供电，8月26日在国家内阁争取到能源技术中立的可靠容量方式，并宣布数据中心须在提交DA前完成社会影响评估并与议会签订社区利益协议。 | https://www.abc.net.au/news/2026-08-24/ai-data-centre-energy-rules-override-qld/107068536
QLD | 2026-08 | SDPWO (Critical Minerals) and Other Legislation Amendment Bill passed (26 Aug 2026) creating 'State strategic projects' but expressly excluding commercial and R&D data centres from that fast-track. | SDPWO (Critical Minerals) and Other Legislation Amendment Bill于2026年8月26日通过，新设“State strategic project”快速通道，但明确排除商业及研发数据中心。 | https://www.minterellison.com/articles/major-reforms-to-fast-track-projects-in-queensland
QLD | 2026-09 | Zerra DC's 2.16 GW Western Downs Digital Park near Dalby (A$31.9 bn) lodged with Western Downs Regional Council, proposing direct Powerlink substation connection and a hybrid gas/renewable supply—the largest test of Queensland's council-DA pathway for hyperscale loads. | Energy Queensland的Large Customer Connection Manual于2026年1月5日生效，整合Energex/Ergon第5章及第5A章大负荷接入程序、时限与成本回收类别。 | https://www.abc.net.au/news/2026-09-14/western-downs-digital-park-data-centre-energy-queensland/107115082
WA | 2026-06 | Western Power published its updated Major Customer Connection Process and quarterly Major Customer Connections Insights Report following its major customer connection review, targeting a more streamlined pathway for large loads and generators. | 国家内阁2026年8月26日通过强制性数据中心标准，西澳已加入；在WEM落地尚待专门立法或规则修改，具体时间未定。 | https://www.westernpower.com.au/resources-education/industry-resources/large-industry-customers-and-generators/major-customer-connection-review/
WA | 2026-07 | The Department of Energy and Economic Diversification released an issues paper (20 July) on DER data and connections reform, including larger DER systems and network capacity sharing; a 4 August consultation paper on Capability Class 2 electric storage resources proposed AEMO powers to set minimum state of charge. | 能源与经济多元化部7月20日发布DER数据及接入改革议题文件，涉及大型DER系统与网络容量共享；8月4日就二类储能资源咨询文件建议赋予AEMO设定最低荷电状态权限。 | https://www.wa.gov.au/system/files/2026-07/issues-paper-der-data-and-connections-reform.pdf
WA | 2026-08 | WA joined National Cabinet's mandatory data centre standards (26 Aug 2026); implementation in the WEM will require separate WA legislation/rule changes, timing not yet announced. | Western Power完成大客户接入审查后，于2026年6月发布更新的《大客户接入程序》及季度《大客户接入洞察报告》，力图为大负荷及发电项目提供更简化路径。 | https://www.claytonutz.com/insights/2026/august/nine-governments-one-rulebook-national-cabinet-backs-mandatory-ai-and-data-centre-standards
SA | 2026-03 | ElectraNet issued its Getting Connected guide (5 and 30 March 2026 versions) with a dedicated load application form, IBL model requirements and system strength charge methodology. | 南澳于2026年8月26日加入国家内阁强制性数据中心标准，并将其可再生电网定位为合规优势。 | https://electranet.com.au/wp-content/uploads/2026/04/New-Customer-Connection-Guide-V1.pdf
SA | 2026-06 | Premier Malinauskas launched the SA data centre strategy (23–24 June 2026) promising a Data Centre and AI Infrastructure Act, Coordinator-General decision pathway, SA Water supply confirmation and Technical Regulator certification; SAPN issued Manual 18 (Connections & Ancillary Network Services). | 州长Malinauskas于2026年6月23–24日发布南澳数据中心战略，承诺出台《数据中心与AI基础设施法》、设立总协调官决策路径、SA Water供水确认及技术监管官认证；SAPN同期发布第18号手册（接入与辅助网络服务）。 | https://w.media/south-australia-proposes-dedicated-data-centre-legislation/
SA | 2025-12 | Late-2025 planning changes moved data centres into an essential-infrastructure style assessment pathway under the PDI Act (State Planning Commission as relevant authority), per Ashurst's summary; the exact Code amendment reference should be confirmed on PlanSA. | ElectraNet于2026年3月发布《接入指南》（5日及30日两版），新增专门的负荷申请表、逆变器型负荷模型要求及系统强度费计算方法。 | https://www.ashurstperkinscoie.com/en/insights/australia-evolving-data-centre-landscape-policy-meets-pipeline/
SA | 2026-08 | SA signed on to National Cabinet's mandatory data centre standards (26 Aug 2026) and positions its renewable grid as the compliance advantage. | 据Ashurst总结，2025年底的规划调整已将数据中心导入PDI法下的基础设施类评估路径（由州规划委员会作为相关审批机构），具体准则修正案编号有待在PlanSA核实。 | https://www.claytonutz.com/insights/2026/august/nine-governments-one-rulebook-national-cabinet-backs-mandatory-ai-and-data-centre-standards
TAS | 2026-09 | Tasmanian Government released Draft Expectations for Data Centres and AI Infrastructure Developers (7 Sept 2026; consultation to 12 Oct 2026): support additional renewable generation, meet share of network/connection costs, protect grid security, use water responsibly, no automatic approvals. | 塔州政府于2026年9月7日发布《数据中心与AI基础设施开发商期望草案》（咨询至10月12日）：要求支持新增可再生发电、承担应分摊的网络/接入成本、保护电网安全、负责任用水，且不设自动批准。 | https://www.premier.tas.gov.au/latest-news/2026/september/clear-expectations-for-data-centres-and-ai-infrastructure
TAS | 2026-09 | A Coordinator-General document revealed six confidential data centre proposals totalling up to 705 MW (including two 200–300 MW AI projects) alongside Firmus' 444 MW Southgate program; many proponents had not yet engaged TasNetworks. | 总协调官文件披露六个保密数据中心提案，合计最多705 MW（含两个200–300 MW的AI项目），另有Firmus公开的444 MW Southgate计划；据报道许多业主尚未接触TasNetworks。 | https://www.examiner.com.au/story/9346904/secret-tassie-ai-data-centre-plans-exposed-in-new-document/
TAS | 2026-08 | Tasmania joined National Cabinet's mandatory data centre standards (26 Aug 2026). | 塔州于2026年8月26日加入国家内阁强制性数据中心标准。 | https://www.claytonutz.com/insights/2026/august/nine-governments-one-rulebook-national-cabinet-backs-mandatory-ai-and-data-centre-standards
ACT | 2026-08 | Chief Minister Barr announced the ACT Data Centre Framework (26 Aug 2026): data centres confined to existing permissible zones, new-renewable offset of additional demand, water-efficiency requirements and preferred corridors; draft Framework with locations and criteria due early 2027. | 首席部长Barr于2026年8月26日宣布《首都领地数据中心框架》：数据中心限于现行允许分区、以新建可再生能源抵消新增需求、设用水效率要求及优先走廊；含选址及标准的框架草案预计2027年初发布。 | https://www.cmtedd.act.gov.au/open_government/inform/act_government_media_releases/barr/2026/providing-a-clear-framework-for-data-centres-in-the-act
ACT | 2026-08 | ACT Government rejected calls for a pause on data centre development and stated its policy already aligns with the National Cabinet standard (23–26 Aug 2026). | 首都领地政府拒绝暂停数据中心开发的呼吁，并于2026年8月23–26日表示其政策已与国家内阁标准一致。 | https://www.abc.net.au/news/2026-08-23/act-data-centre-policy-already-aligned-with-national-ai-standard/106936530
ACT | 2026-08 | Transgrid's NSW Network Capacity Allocation Policy (14 Aug 2026) indirectly affects ACT loads ≥30 MW that depend on Transgrid's Canberra/Williamsdale supply points. | Transgrid新州《网络容量分配政策》（2026年8月14日）间接影响依赖Transgrid堪培拉/Williamsdale供电点的30 MW及以上首都领地负荷。 | https://w.media/transgrid-sets-six-tests-for-data-centres-seeking-nsw-grid-capacity/
NT | 2026-07 | NT Government granted Beetaloo Digital 185 ha at Weddell with 12-month exclusivity for a proposed 2 GW, A$40 bn gas-powered hyperscale campus (22 July 2026); up to 12 developers reported to be enquiring, with no published NT data centre policy. | 北领地与昆州在2026年8月26日国家内阁数据中心框架中争取到"能源技术中立"的可靠容量方式，允许燃气支撑供电。 | https://ntindependent.com.au/nt-government-backs-proposed-2gw-data-centre-at-weddell/
NT | 2026-07 | Hyperscalers publicly targeted the NT for gas-backed capacity and subsea-cable proximity (ABC, 13 July 2026), prompting debate on grid impact given the Weddell proposal would use six times the Top End's annual consumption. | 北领地政府于2026年7月22日授予Beetaloo Digital位于Weddell的185公顷土地并附12个月独家权，用于拟建2 GW、400亿澳元的燃气超大规模园区；据报道多达12家开发商正在咨询，但北领地目前无公开数据中心政策。 | https://www.abc.net.au/news/2026-07-13/data-centre-hyperscalers-target-northern-territory/106898282
NT | 2026-08 | NT, with Queensland, secured an 'energy-agnostic' firming approach in the National Cabinet data centre framework (26 Aug 2026) allowing gas-backed supply. | 超大规模运营商公开瞄准北领地的燃气支撑容量及海底光缆邻近优势（ABC，2026年7月13日）；鉴于Weddell提案用电量将达北端地区年用电量六倍，引发对电网影响的讨论。 | https://www.claytonutz.com/insights/2026/august/nine-governments-one-rulebook-national-cabinet-backs-mandatory-ai-and-data-centre-standards
FED | 2026-09 | PM&C released the consultation paper 'Getting it right: Building AI infrastructure that works for Australia' on 17 September 2026, putting tiered capacity thresholds on the mandatory national data centre standards for the first time - under 30 MW out of scope, 30-100 MW baseline obligations, above 100 MW (or a 150 MW cumulative portfolio) substantial obligations - with submissions closing 9 October 2026. | PM&C于2026年9月17日发布咨询文件《Getting it right: Building AI infrastructure that works for Australia》，首次给出全国强制标准的分级门槛：30 MW以下不适用、30–100 MW适用基础义务、100 MW以上（或组合容量150 MW以上）适用加强义务，意见征集至10月9日。 | https://www.pmc.gov.au/resources/getting-it-right-building-ai-infrastructure-works-australia
FED | 2026-09 | The consultation paper confirms the Commonwealth will legislate minimum standards covering renewable matching, firming, demand flexibility, PUE and WUE performance and a 'no net costs' principle, with the Clean Energy Regulator administering certificate compliance and states free to impose more stringent requirements but not to water them down. | 咨询文件确认联邦将就可再生电量匹配、可靠容量、需求灵活性、PUE与WUE绩效及"不增加其他用户成本"原则立法设定最低标准，证书合规由Clean Energy Regulator执行；各州可加码但不得削弱。 | https://www.claytonutz.com/insights/2026/september/regulation-of-data-centres-and-ai-training-the-commonwealth-asks-the-hard-questions
FED | 2026-09 | The AEMC initiated both of Minister Bowen's network cost-recovery rule changes (ERC0448 Package 1 and Package 2) on 24 September 2026 under a single consultation paper, with submissions closing 5 November 2026, a draft determination due 1 April 2027 and completion scheduled for 22 July 2027. | AEMC于2026年9月24日以一份合并咨询文件同时启动Bowen部长提交的两项网络成本回收规则修改（ERC0448第一批及第二批），意见征集至11月5日，初步裁定定于2027年4月1日，预计2027年7月22日完成。 | https://www.aemc.gov.au/rule-changes/cost-recovery-network-augmentations-package-1
NSW | 2026-09 | The Electricity Infrastructure Investment Amendment Bill 2026, which lets the Minister declare large load access schemes for infrastructure of 5 MW or more, passed the Legislative Assembly on 15 September 2026 and now sits with the Legislative Council. | 授权部长对5 MW及以上设施宣布大负荷接入计划的Electricity Infrastructure Investment Amendment Bill 2026，于2026年9月15日通过新州众议院，现待上议院审议。 | https://blog.kreisson.com.au/the-pulse/the-pulse-17-september-2026
QLD | 2026-10 | Queensland announced on 2 October 2026 that data centre development applications will be assessed by the State through SARA rather than by local councils, using the framework applied to renewable energy projects since July 2025, with a social impact assessment and a community benefit agreement required before lodgement and the amending regulation and size thresholds still to be published. | 昆州于2026年10月2日宣布，数据中心开发申请改由州级SARA评估而非地方议会，沿用2025年7月起适用于可再生能源项目的框架；申请前须完成社会影响评估并与议会签订社区利益协议，修订条例与适用门槛尚未公布。 | https://www.abc.net.au/news/2026-10-02/qld-state-to-take-data-centre-approvals-from-local-councils/107221348
NT | 2026-09 | The NT Government's submission of 25 September 2026 rejects any mandatory requirement for data centres to fully offset demand with new renewable generation, proposing instead dedicated standalone generation outside the regulated system - including Territory gas - and outcomes-based, technology-neutral national standards. | 北领地政府在2026年9月25日的意见中反对强制要求数据中心以新建可再生发电全额抵消用电，主张采用独立于受监管电力系统之外的专用电源（含本地天然气），并要求全国标准以结果为导向、技术中立。 | https://w.media/northern-territory-challenges-proposed-australias-data-centre-energy-rules/
SA | 2026-10 | The terms of reference for South Australia's AI Royal Commission were signed by the Governor on 1 October 2026 and expressly exclude data centre matters, while the Data Centre and AI Infrastructure Bill announced on 23 June 2026 remains unintroduced. | 南澳AI Royal Commission的职权范围于2026年10月1日由总督签署，明确将数据中心事项排除在外；2026年6月23日宣布的Data Centre and AI Infrastructure Bill仍未提交州议会。 | https://certifiedstrategic.com/insights/south-australia-ai-royal-commission-data-centres-out-of-scope
VIC | 2026-09 | Victoria published the Sustainable Data Centre Action Plan on 22 September 2026, creating a stand-alone 'data centre' planning land-use term, prohibiting the use in residential and Green Wedge zones with a 150 m buffer from dwellings, requiring operators to offset operational electricity with new renewable generation and storage and to fund all connection and augmentation costs, setting design WUE of 1.0 (potable) or 1.6 (non-potable), and making VicGrid a statutory referral authority for every data centre application. | 维州于2026年9月22日发布Sustainable Data Centre Action Plan：设立独立的"data centre"规划用途术语，住宅区及Green Wedge Zone禁止并与住宅建筑保持150米退让；运营商须以新建可再生发电加储能抵消运营用电，并自行承担全部接入与扩建费用；设计WUE不高于1.0（自来水）或1.6（非饮用水）；VicGrid成为所有数据中心申请的法定转介机构。 | https://djsir.vic.gov.au/priorities-and-initiatives/ai-mission-statement/sustainable-data-centre-action-plan

## Infrastructure
infra_id | name | category | state | lat | lng | operator | voltage_kv | capacity_notes | relevance_en | relevance_zh | source
TS-SYDW | Sydney West 330 kV Substation | Terminal Station/Substation (≥220kV) | NSW | -33.8161 | 150.8279 | Transgrid | 330 | 330/132 kV bulk supply point; 500 kV Bannaby & Mt Piper lines; adjacent to 132 kV Eastern Creek subs | Anchor supply point for the Eastern Creek / Erskine Park hyperscale cluster (NEXTDC S7, AirTrunk SYD1, Equinix, Microsoft). | Eastern Creek / Erskine Park超大规模集群（NEXTDC S7、AirTrunk SYD1、Equinix、微软）的核心供电节点，330/132 kV枢纽，上接Bannaby与Mt Piper两条500 kV线路。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-MAMR | Mamre 330 kV Substation | Terminal Station/Substation (≥220kV) | NSW | -33.8119 | 150.7954 | Transgrid | 330 | New 330/132 kV substation (commissioned 2020s) at Erskine Park to relieve Sydney West | Second 330 kV injection point for the Mamre Road / Erskine Park industrial precinct where multiple 100 MW+ campuses are proposed. | Erskine Park新建的330/132 kV变电站，为Mamre Road工业区提供第二个330 kV注入点、分担Sydney West负荷，多个百兆瓦级园区拟在此接入。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-KEMP | Kemps Creek 500 kV Substation | Terminal Station/Substation (≥220kV) | NSW | -33.9006 | 150.8085 | Transgrid | 500 | 500/330 kV switching station on Bannaby–Sydney West corridor; near Western Sydney Aerotropolis | Highest-voltage node in Western Sydney; key to powering the Aerotropolis / Bradfield data-centre precinct. | 西悉尼电压等级最高的节点，位于Bannaby–Sydney West 500 kV走廊，Aerotropolis / Bradfield数据中心园区的供电取决于此。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-SYDN | Sydney North 330 kV Substation | Terminal Station/Substation (≥220kV) | NSW | -33.6556 | 151.0301 | Transgrid | 330 | 330/132 kV bulk supply (Dural/Kenthurst); feeds northern Sydney 132 kV network | Upstream source for Macquarie Park / North Ryde 132 kV zone substations serving NEXTDC S1/S2/S5 and Macquarie Telecom. | Dural / Kenthurst一带的330/132 kV枢纽，向北悉尼132 kV网络供电，是Macquarie Park / North Ryde区域变电站（服务NEXTDC S1/S2/S5和Macquarie Telecom）的上游电源。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-SYDE | Sydney East 330 kV Substation | Terminal Station/Substation (≥220kV) | NSW | -33.7258 | 151.2083 | Transgrid | 330 | 330/132 kV bulk supply at Belrose; supplies northern beaches & lower north shore | Feeds the Artarmon / St Leonards 132 kV area (NEXTDC S3/S6, Global Switch-adjacent zone) and the northern-beaches cable landing area. | 位于Belrose的330/132 kV枢纽，向Artarmon / St Leonards 132 kV片区（NEXTDC S3/S6及Global Switch旧址周边）和北海滩海缆登陆区供电。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-SYDS | Sydney South 330 kV Substation | Terminal Station/Substation (≥220kV) | NSW | -33.9786 | 151.0129 | Transgrid | 330 | 330/132 kV bulk supply at Picnic Point; south-west Sydney | Bulk supply for south-western Sydney 132 kV subs including areas around Bankstown/Milperra industrial DC sites. | Picnic Point的330/132 kV枢纽，覆盖悉尼西南132 kV网络，是Bankstown / Milperra工业区数据中心选址的上游电源。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-ROOK | Rookwood Road 330 kV Substation | Terminal Station/Substation (≥220kV) | NSW | -33.8942 | 151.037 | Transgrid | 330 | 330/132 kV bulk supply, Potts Hill/Yagoona; underground 330 kV cables to Sydney South & Haymarket | Inner-west bulk supply point close to the Silverwater / Homebush / Lidcombe DC sites (AirTrunk SYD2-adjacent area). | Potts Hill / Yagoona的330/132 kV枢纽，以330 kV地下电缆连接Sydney South和Haymarket，紧邻Silverwater / Homebush / Lidcombe一带（AirTrunk SYD2周边）的数据中心选址。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-BEAC | Beaconsfield 330 kV Substation | Terminal Station/Substation (≥220kV) | NSW | -33.9151 | 151.1872 | Transgrid/Ausgrid | 330 | 330/132 kV underground-fed substation in Alexandria | Sits inside the Alexandria/Mascot carrier-hotel cluster (Equinix SY3/SY4/SY5, Southern Cross CLS) - the densest interconnection zone in Australia. | Alexandria的地下电缆供电330/132 kV变电站，处于Alexandria / Mascot运营商中立机房集群（Equinix SY3/SY4/SY5、Southern Cross登陆站）之中，这里是全澳互联密度最高的区域。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-HAYM | Haymarket 330 kV Substation | Terminal Station/Substation (≥220kV) | NSW | -33.8814 | 151.2022 | Transgrid/Ausgrid | 330 | 330/132 kV indoor GIS substation supplying Sydney CBD | Supplies the Sydney CBD exchanges and carrier hotels (Pitt St, Kent St, DigiCo 400 Harris St). | 供电悉尼CBD的330/132 kV室内GIS变电站，覆盖Pitt St、Kent St交换局及DigiCo 400 Harris St等市中心运营商中立机房。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-HOLR | Holroyd 330 kV Substation | Terminal Station/Substation (≥220kV) | NSW | -33.8347 | 150.9192 | Transgrid | 330 | 330/132 kV bulk supply at Greystanes | Bulk supply between Parramatta and Eastern Creek; backs up the Huntingwood / Arndell Park DC sites. | Greystanes的330/132 kV枢纽，介于Parramatta与Eastern Creek之间，为Huntingwood / Arndell Park数据中心选址提供备用电源。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-LIVP | Liverpool 330 kV Substation | Terminal Station/Substation (≥220kV) | NSW | -33.9327 | 150.8658 | Transgrid | 330 | 330/132 kV bulk supply at Prestons | Serves the Prestons / Moorebank logistics belt being targeted for large DC campuses. | Prestons的330/132 kV枢纽，覆盖Prestons / Moorebank物流带，多个大型数据中心园区正瞄准这一区域。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-VINE | Vineyard 330 kV Substation | Terminal Station/Substation (≥220kV) | NSW | -33.6571 | 150.8435 | Transgrid | 330 | 330/132 kV bulk supply, north-west growth area | Closest 330 kV source to the Marsden Park / Riverstone north-west Sydney DC proposals. | 悉尼西北增长区的330/132 kV枢纽，是Marsden Park / Riverstone数据中心提案最近的330 kV电源。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-BANN | Bannaby 500 kV Substation | Terminal Station/Substation (≥220kV) | NSW | -34.4417 | 150.0511 | Transgrid | 500 | 500/330 kV hub; HumeLink terminal; Sydney West & Kemps Creek 500 kV lines | Gateway that brings Snowy 2.0 / southern NSW renewables into Sydney - determines long-run firm supply for Sydney DCs. | 500/330 kV枢纽兼HumeLink终端，以500 kV线路连接Sydney West和Kemps Creek，Snowy 2.0及新州南部可再生能源经此送入悉尼，决定悉尼数据中心的长期可靠供电。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-YASS | Yass 330 kV Substation | Terminal Station/Substation (≥220kV) | NSW | -34.8626 | 148.9041 | Transgrid | 330 | 330 kV hub on Snowy–Sydney corridor; feeds Canberra | Key node for Canberra-region supply and for regional DC proposals along the Hume corridor. | Snowy–悉尼输电走廊上的330 kV枢纽，向堪培拉供电，也是Hume走廊沿线区域性数据中心提案的关键节点。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
ZS-ECRK | Eastern Creek 132 kV Zone Substation | Terminal Station/Substation (132/110/66kV) | NSW | -33.8133 | 150.8368 | Endeavour Energy | 132 | 132 kV zone sub adjacent to Sydney West; Eastern Creek North (-33.80293,150.84006) also 132 kV | Direct 132 kV connection point for the Eastern Creek hyperscale campuses. | 紧邻Sydney West的132 kV区域变电站（Eastern Creek North亦为132 kV），Eastern Creek超大规模园区的直接接入点。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
ZS-MACQ | Macquarie Park 132 kV Zone Substation | Terminal Station/Substation (132/110/66kV) | NSW | -33.7867 | 151.1329 | Ausgrid | 132 | 132/11 kV zone substation | Supplies NEXTDC S1, S2, S5, Macquarie Telecom IC1-IC3 and Fujitsu North Ryde. | 132/11 kV区域变电站，供电NEXTDC S1、S2、S5、Macquarie Telecom IC1–IC3及Fujitsu North Ryde。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
ZS-LANE | Lane Cove 132 kV Substation | Terminal Station/Substation (132/110/66kV) | NSW | -33.8117 | 151.1451 | Ausgrid | 132 | 132 kV substation, Lane Cove West | Second 132 kV source for the Lane Cove / Macquarie Park data-centre corridor. | Lane Cove West的132 kV变电站，为Lane Cove / Macquarie Park数据中心走廊提供第二路132 kV电源。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
ZS-WILL | Willoughby 132 kV Substation (Artarmon) | Terminal Station/Substation (132/110/66kV) | NSW | -33.8168 | 151.1854 | Ausgrid | 132 | 132 kV sub in Artarmon industrial area | Supplies the Artarmon cluster (NEXTDC S3 80 MW, S6, Global Switch-era sites). | Artarmon工业区的132 kV变电站，供电Artarmon集群（NEXTDC S3 80 MW、S6及Global Switch时期的站点）。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
ZS-MARS | Marsden Park 132 kV Zone Substation | Terminal Station/Substation (132/110/66kV) | NSW | -33.6924 | 150.8258 | Endeavour Energy | 132 | 132 kV zone sub; South Marsden Park also 132 kV (-33.72108,150.83318) | Nearest zone substation to the Marsden Park / Sydney Business Park DC proposals. | 132 kV区域变电站（South Marsden Park亦为132 kV），是距Marsden Park / Sydney Business Park数据中心提案最近的接入点。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-KEIL | Keilor Terminal Station | Terminal Station/Substation (≥220kV) | VIC | -37.7382 | 144.8462 | AusNet (transmission) | 500 | 500/220 kV terminal; Sydenham–Keilor 500 kV; feeds Melbourne west/north-west | Backbone terminal for the Melbourne Airport / Tullamarine DC cluster (NEXTDC M2, AirTrunk MEL1, Equinix ME2). | 500/220 kV终端站，经Sydenham–Keilor 500 kV线路供电墨尔本西部和西北部，是墨尔本机场 / Tullamarine数据中心集群（NEXTDC M2、AirTrunk MEL1、Equinix ME2）的骨干电源。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-SYDM | Sydenham Terminal Station | Terminal Station/Substation (≥220kV) | VIC | -37.6761 | 144.7472 | AusNet (transmission) | 500 | 500/220 kV terminal; Moorabool–Sydenham 500 kV; western Melbourne growth corridor | Highest-capacity injection point for western Melbourne; anchors the Truganina / Derrimut / Ravenhall DC land bank. | Moorabool–Sydenham 500 kV线路的500/220 kV终端站，墨尔本西部容量最大的注入点，支撑Truganina / Derrimut / Ravenhall的数据中心土地储备。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-DEER | Deer Park Terminal Station | Terminal Station/Substation (≥220kV) | VIC | -37.7772 | 144.735 | AusNet (transmission) | 220 | 220/66 kV terminal at Ravenhall | Direct 220 kV supply for the Deer Park / Derrimut industrial DC sites. | Ravenhall的220/66 kV终端站，为Deer Park / Derrimut工业区数据中心选址提供直接220 kV电源。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-BROK | Brooklyn Terminal Station | Terminal Station/Substation (≥220kV) | VIC | -37.8259 | 144.8618 | AusNet (transmission) | 220 | 220/66 kV terminal, Altona North; inner-west | Supplies West Footscray / Sunshine (NEXTDC M3 225 MW) and Port Melbourne west. | Altona North的220/66 kV终端站，覆盖墨尔本内西区，供电West Footscray / Sunshine（NEXTDC M3 225 MW）及Port Melbourne西侧。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-WMEL | West Melbourne Terminal Station | Terminal Station/Substation (≥220kV) | VIC | -37.8003 | 144.9349 | AusNet (transmission) | 220 | 220/66 kV terminal, Kensington; CBD and Docklands supply | Supplies Melbourne CBD carrier hotels (530 Collins St, Exhibition St exchange) and Docklands. | Kensington的220/66 kV终端站，向墨尔本CBD和Docklands供电，覆盖530 Collins St、Exhibition St交换局等市中心运营商中立机房。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-FISH | Fishermans Bend Terminal Station | Terminal Station/Substation (≥220kV) | VIC | -37.8252 | 144.9294 | AusNet (transmission) | 220 | 220/66 kV terminal, Port Melbourne | Supplies the Port Melbourne DC precinct (NEXTDC M1/M4, Equinix ME1/ME2, Digital Realty). | Port Melbourne的220/66 kV终端站，供电Port Melbourne数据中心片区（NEXTDC M1/M4、Equinix ME1/ME2、Digital Realty）。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-TEMP | Templestowe Terminal Station | Terminal Station/Substation (≥220kV) | VIC | -37.7481 | 145.1705 | AusNet (transmission) | 220 | 220/66 kV terminal, Doncaster East; eastern suburbs | Eastern Melbourne bulk supply; relevant to Nunawading / Ringwood edge sites. | Doncaster East的220/66 kV终端站，墨尔本东部的主供电点，与Nunawading / Ringwood边缘站点相关。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-ROWV | Rowville Terminal Station | Terminal Station/Substation (≥220kV) | VIC | -37.9293 | 145.2273 | AusNet (transmission) | 500 | 500/220 kV terminal; Hazelwood–Rowville 500 kV; south-east Melbourne | Brings Latrobe Valley power into south-east Melbourne; backbone for Dandenong South / Clayton DC proposals. | Hazelwood–Rowville 500 kV线路的500/220 kV终端站，将Latrobe Valley电力送入墨尔本东南部，是Dandenong South / Clayton数据中心提案的骨干电源。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-SPRV | Springvale Terminal Station | Terminal Station/Substation (≥220kV) | VIC | -37.9282 | 145.1461 | AusNet (transmission) | 220 | 220/66 kV terminal | Supplies Clayton / Mulgrave / Springvale tech precinct. | 220/66 kV终端站，供电Clayton / Mulgrave / Springvale科技园区。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-CRAN | Cranbourne Terminal Station | Terminal Station/Substation (≥220kV) | VIC | -38.0856 | 145.2664 | AusNet (transmission) | 500 | 500/220 kV terminal, Cranbourne West | Southern 500 kV node; supports growth-corridor DC sites around Cranbourne / Dandenong South. | Cranbourne West的500/220 kV终端站，墨尔本南部的500 kV节点，支撑Cranbourne / Dandenong South增长走廊的数据中心选址。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-THOM | Thomastown Terminal Station | Terminal Station/Substation (≥220kV) | VIC | -37.6937 | 145.0099 | AusNet (transmission) | 220 | 220/66 kV terminal; northern suburbs | Bulk supply for the Thomastown / Epping industrial belt. | 墨尔本北郊的220/66 kV终端站，Thomastown / Epping工业带的主供电点。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-SMOR | South Morang Terminal Station | Terminal Station/Substation (≥220kV) | VIC | -37.6445 | 145.0784 | AusNet (transmission) | 500 | 500/330/220 kV hub; NSW–VIC interconnector terminal | Northern 500 kV hub tying Victoria to NSW; key for firm supply into Melbourne's north. | 500/330/220 kV枢纽兼新州–维州联络线终端，墨尔本北部的500 kV中枢，关系到墨尔本北部的可靠供电。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-TYAB | Tyabb Terminal Station | Terminal Station/Substation (≥220kV) | VIC | -38.2679 | 145.2016 | AusNet (transmission) | 220 | 220/66 kV terminal, Mornington Peninsula | Supply point for Mornington Peninsula / Frankston south edge sites. | Mornington Peninsula的220/66 kV终端站，Mornington Peninsula / Frankston南部边缘站点的供电点。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-ROCK | Rocklea 275 kV Substation | Terminal Station/Substation (≥220kV) | QLD | -27.5529 | 152.9993 | Powerlink | 275 | 275/110 kV bulk supply, south-west Brisbane | Nearest bulk supply to the Rocklea / Acacia Ridge / Archerfield DC sites (Polaris-adjacent). | 布里斯班西南的275/110 kV枢纽，距Rocklea / Acacia Ridge / Archerfield数据中心选址（Polaris周边）最近的主供电点。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-BELM | Belmont 275 kV Substation | Terminal Station/Substation (≥220kV) | QLD | -27.537 | 153.1152 | Powerlink | 275 | 275/110 kV bulk supply, Mansfield/Belmont; eastern Brisbane | Supplies the Murarrie / Eagle Farm / Brisbane Airport DC corridor (AirTrunk BNE, NEXTDC B2 area). | Mansfield / Belmont的275/110 kV枢纽，覆盖布里斯班东部，供电Murarrie / Eagle Farm / 布里斯班机场数据中心走廊（AirTrunk BNE、NEXTDC B2一带）。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-SPIN | South Pine 275 kV Substation | Terminal Station/Substation (≥220kV) | QLD | -27.3235 | 152.9701 | Powerlink | 275 | 275/110 kV hub, Brendale; northern Brisbane | Key northern hub; feeds Brendale / Strathpine industrial estates and the Aspley NBN aggregation nodes. | Brendale的275/110 kV枢纽，布里斯班北部的核心节点，供电Brendale / Strathpine工业区及Aspley的NBN汇聚节点。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-LOGA | Loganlea 275 kV Substation | Terminal Station/Substation (≥220kV) | QLD | -27.6643 | 153.1315 | Powerlink | 275 | 275/110 kV bulk supply, Meadowbrook | Bulk supply for Logan / Yatala corridor DC land. | Meadowbrook的275/110 kV枢纽，Logan / Yatala走廊数据中心用地的主供电点。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-SWAN | Swanbank E 275 kV Substation | Terminal Station/Substation (≥220kV) | QLD | -27.6551 | 152.819 | Powerlink/CleanCo | 275 | 275 kV switchyard at Swanbank power station precinct (Swanbank B non-operational) | Ipswich/Swanbank precinct is marketed for large DC and BESS co-location with existing 275 kV connection. | Swanbank电厂区的275 kV开关站（Swanbank B已停运），Ipswich / Swanbank片区正以现成275 kV接入为卖点，招引大型数据中心与BESS共址项目。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-GRNB | Greenbank 275 kV Substation | Terminal Station/Substation (≥220kV) | QLD | -27.7323 | 152.9564 | Powerlink | 275 | 275/110 kV hub, Greenbank; south of Brisbane | Southern hub between Brisbane and Gold Coast; near Greater Flagstone growth area. | Greenbank的275/110 kV枢纽，位于布里斯班与黄金海岸之间，邻近Greater Flagstone增长区。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-MOLE | Molendinar 275 kV Substation | Terminal Station/Substation (≥220kV) | QLD | -27.9784 | 153.3601 | Powerlink | 275 | 275/110 kV bulk supply, Gold Coast | Main bulk supply for the Gold Coast (NEXTDC GC1, Southport POI). | 黄金海岸的275/110 kV枢纽，黄金海岸的主供电点（NEXTDC GC1、Southport POI）。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-ABER | Abermain 275 kV Substation | Terminal Station/Substation (≥220kV) | QLD | -27.5771 | 152.7716 | Powerlink | 275 | 275/110 kV bulk supply, Tivoli/Ipswich | Second 275 kV source for the Ipswich DC precinct. | Tivoli / Ipswich的275/110 kV枢纽，Ipswich数据中心片区的第二路275 kV电源。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-KWIN | Kwinana Terminal | Terminal Station/Substation (≥220kV) | WA | -32.2003 | 115.7761 | Western Power | 330 | 330/132 kV terminal at Naval Base; also 132 kV yard (-32.19763,115.77655) | Southern anchor of the SWIS 330 kV ring; supplies Kwinana industrial DC/BESS sites. | Naval Base的330/132 kV终端站（另有132 kV开关场），SWIS 330 kV环网的南端锚点，供电Kwinana工业区的数据中心与BESS选址。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-STER | Southern Terminal | Terminal Station/Substation (≥220kV) | WA | -32.0954 | 115.8444 | Western Power | 330 | 330/132 kV terminal, Bibra Lake | Bulk supply for Perth's southern suburbs incl. Bibra Lake / Jandakot / Canning Vale DC sites. | Bibra Lake的330/132 kV终端站，珀斯南郊的主供电点，覆盖Bibra Lake / Jandakot / Canning Vale数据中心选址。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-NTER | Northern Terminal | Terminal Station/Substation (≥220kV) | WA | -31.8539 | 115.8922 | Western Power | 330 | 330/132 kV terminal, Malaga | Bulk supply for NEXTDC P1 (Malaga) and Wangara / Balcatta industrial DC sites. | Malaga的330/132 kV终端站，NEXTDC P1（Malaga）及Wangara / Balcatta工业区数据中心选址的主供电点。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-CANN | Cannington Terminal | Terminal Station/Substation (132/110/66kV) | WA | -32.0189 | 115.9424 | Western Power | 132 | 132 kV terminal | Supplies Cannington / Welshpool / Bentley (Bentley NBN depot, Curtin precinct). | 132 kV终端站，供电Cannington / Welshpool / Bentley（Bentley NBN节点、Curtin园区）。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-EPER | East Perth Terminal | Terminal Station/Substation (132/110/66kV) | WA | -31.9457 | 115.879 | Western Power | 132 | 132 kV terminal supplying CBD | Supplies Perth CBD carrier hotels (NEXTDC P2, Vocus 1 William St, Wellington St exchange). | 供电珀斯CBD的132 kV终端站，覆盖NEXTDC P2、Vocus 1 William St及Wellington St交换局等市中心机房。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-WTER | Western Terminal | Terminal Station/Substation (132/110/66kV) | WA | -31.9566 | 115.7903 | Western Power | 132 | 132 kV terminal, Mount Claremont | Closest terminal to the Floreat / City Beach cable landing area and Equinix PE2 Shenton Park. | Mount Claremont的132 kV终端站，距Floreat / City Beach海缆登陆区及Equinix PE2（Shenton Park）最近。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-TORR | Torrens Island 275 kV Substation | Terminal Station/Substation (≥220kV) | SA | -34.8079 | 138.5232 | ElectraNet | 275 | 275 kV switchyards A & B at Torrens Island PS; Torrens Island BESS | Adelaide's main generation/transmission hub; Port Adelaide / Gillman DC proposals connect here. | Torrens Island电厂的275 kV A、B开关场（含Torrens Island BESS），阿德莱德的发电与输电主枢纽，Port Adelaide / Gillman数据中心提案在此接入。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-MAGI | Magill 275 kV Substation | Terminal Station/Substation (≥220kV) | SA | -34.9108 | 138.682 | ElectraNet | 275 | 275/66 kV, eastern Adelaide | Eastern bulk supply for Adelaide CBD (NEXTDC A1, Colocity, DigiCo ADL2 Hawthorn). | 阿德莱德东部的275/66 kV变电站，阿德莱德CBD（NEXTDC A1、Colocity、DigiCo ADL2 Hawthorn）的东侧主供电点。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-CHER | Cherry Gardens 275 kV Substation | Terminal Station/Substation (≥220kV) | SA | -35.095 | 138.6459 | ElectraNet | 275 | 275/66 kV, southern Adelaide Hills | Southern bulk supply for Adelaide (Lonsdale NBN depot, Tonsley precinct). | 阿德莱德山南部的275/66 kV变电站，阿德莱德南部的主供电点（Lonsdale NBN节点、Tonsley园区）。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-PARA | Para 275 kV Substation | Terminal Station/Substation (≥220kV) | SA | -34.7357 | 138.7119 | ElectraNet | 275 | 275/66 kV hub, Gould Creek; northern Adelaide | Northern hub feeding Edinburgh Parks (DigiCo ADL1) and Elizabeth industrial land. | Gould Creek的275/66 kV枢纽，阿德莱德北部的核心节点，供电Edinburgh Parks（DigiCo ADL1）和Elizabeth工业用地。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-GEOT | George Town 220 kV Substation | Terminal Station/Substation (≥220kV) | TAS | -41.1285 | 146.8853 | TasNetworks | 220 | 220/110 kV; Basslink & Marinus Link converter site, Bell Bay | Landing point for Basslink/Marinus; Bell Bay is Tasmania's prime hydro-powered DC/hydrogen precinct. | Bell Bay的220/110 kV变电站，Basslink与Marinus Link换流站所在地，Bell Bay是塔州依托水电的首选数据中心/氢能园区。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-PALM | Palmerston 220 kV Substation | Terminal Station/Substation (≥220kV) | TAS | -41.7873 | 146.9902 | TasNetworks | 220 | 220 kV hub, Poatina; northern midlands | Central Tasmanian transmission hub linking hydro schemes to Launceston/Bell Bay. | Poatina的220 kV枢纽，塔州中部输电中枢，连接各水电站与Launceston / Bell Bay。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-CHAP | Chapel Street 220 kV Substation | Terminal Station/Substation (≥220kV) | TAS | -42.8431 | 147.255 | TasNetworks | 220 | 220/110 kV, Glenorchy; Hobart supply | Main bulk supply for Hobart (TasmaNet DC3 Dowsing Point, 7HOB POI). | Glenorchy的220/110 kV变电站，霍巴特的主供电点（TasmaNet DC3 Dowsing Point、7HOB POI）。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-HUDS | Hudson Creek 132 kV Substation | Terminal Station/Substation (132/110/66kV) | NT | -12.4589 | 130.932 | Power and Water Corp | 132 | 132 kV hub, Wishart/Berrimah; Darwin-Katherine system | Primary Darwin bulk supply; adjacent to Darwin CLS and the Middle Arm / East Arm industrial DC proposals. | Wishart / Berrimah的132 kV枢纽，Darwin–Katherine电网的主供电点，紧邻达尔文海缆登陆站及Middle Arm / East Arm工业区数据中心提案。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
TS-CHAN | Channel Island 132 kV Substation | Terminal Station/Substation (132/110/66kV) | NT | -12.5559 | 130.867 | Territory Generation/PWC | 132 | 132 kV switchyard at Channel Island power station | Darwin's main generation node; relevant for the proposed Darwin subsea-cable hub DCs. | Channel Island电厂的132 kV开关场，达尔文的主发电节点，与拟建的达尔文海缆枢纽数据中心相关。 | Geoscience Australia Electricity Infrastructure (services.ga.gov.au .../Electricity_Infrastructure/MapServer/0), CC BY 4.0, queried 2026-09-15
PS-ERAR | Eraring Power Station | Power Station (major) | NSW | -33.0621 | 151.5206 | Origin Energy | 500 | 2,880 MW coal; 500/330 kV; closure deferred to 2027-29 | Largest NSW generator; its retirement timing drives Sydney's firm-capacity risk for DCs. | 新州最大的发电机组（2,880 MW燃煤，500/330 kV），关停已推迟至2027–29年，其退役节奏直接决定悉尼数据中心的可靠容量风险。 | Geoscience Australia Electricity Infrastructure MapServer/1 (Major Power Stations), CC BY 4.0, queried 2026-09-15
PS-BAYS | Bayswater Power Station | Power Station (major) | NSW | -32.3953 | 150.9491 | AGL | 500 | 2,640 MW coal; 500/330 kV hub; Hunter Energy Hub | Hunter Valley 500 kV hub; site of AGL's Hunter Energy Hub incl. proposed DC/BESS co-location. | 2,640 MW燃煤电站，Hunter Valley的500 kV枢纽，AGL Hunter Energy Hub所在地，拟建数据中心与BESS共址项目。 | Geoscience Australia Electricity Infrastructure MapServer/1 (Major Power Stations), CC BY 4.0, queried 2026-09-15
PS-MTPI | Mt Piper Power Station | Power Station (major) | NSW | -33.3589 | 150.0313 | EnergyAustralia | 500 | 1,400 MW coal; 500/330 kV | Western 500 kV source into Sydney West / Bannaby corridor. | 1,400 MW燃煤电站（500/330 kV），Sydney West / Bannaby走廊的西侧500 kV电源。 | Geoscience Australia Electricity Infrastructure MapServer/1 (Major Power Stations), CC BY 4.0, queried 2026-09-15
PS-LOYA | Loy Yang A Power Station | Power Station (major) | VIC | -38.2536 | 146.5746 | AGL | 500 | 2,180 MW coal; Latrobe Valley 500 kV hub (Loy Yang B 1,000 MW adjacent) | Latrobe Valley 500 kV hub feeding Rowville/Cranbourne; earmarked for post-coal DC and hydrogen reuse. | 2,180 MW燃煤电站（相邻Loy Yang B 1,000 MW），Latrobe Valley的500 kV枢纽，供电Rowville / Cranbourne，煤电退出后拟转型为数据中心与氢能用途。 | Geoscience Australia Electricity Infrastructure MapServer/1 (Major Power Stations), CC BY 4.0, queried 2026-09-15
PS-TORB | Torrens Island B Power Station | Power Station (major) | SA | -34.8052 | 138.5226 | AGL | 275 | 800 MW gas + 250 MW BESS on site | Adelaide's main dispatchable plant; co-located BESS and 275 kV switchyard. | 阿德莱德的主力可调度机组（800 MW燃气），场内配有250 MW BESS和275 kV开关场。 | Geoscience Australia Electricity Infrastructure MapServer/1 (Major Power Stations), CC BY 4.0, queried 2026-09-15
PS-TARO | Tarong Power Station | Power Station (major) | QLD | -26.7823 | 151.9153 | Stanwell | 275 | 1,400 MW coal (+ Tarong North 443 MW); 275 kV | Major SEQ generator; 275 kV lines into South Pine / Brisbane west. | 昆州东南部的主力电站（1,400 MW燃煤，另有Tarong North 443 MW），以275 kV线路接入South Pine和布里斯班西部。 | Geoscience Australia Electricity Infrastructure MapServer/1 (Major Power Stations), CC BY 4.0, queried 2026-09-15
CLS-OXF | Oxford Falls Cable Landing Station | Cable Landing Station | NSW | -33.7345 | 151.244 | Telstra (AJC) / Vocus (TGA) |  | AJC (2001, upgraded), Tasman Global Access (2017) | Trans-Pacific/Tasman landing on Sydney's northern beaches; AJC backhaul to Paddington and Sydney CBD. | 悉尼北海滩的跨太平洋/塔斯曼海缆登陆站（AJC 2001年、Tasman Global Access 2017年），AJC经此回传至Paddington和悉尼CBD。 | TeleGeography Submarine Cable Map API v3 (submarinecablemap.com/api/v3), landing-point-geo.json + country/australia.json, 2026-09-15; CLS building position approximate
CLS-PAD | Paddington Cable Landing Station (Telstra exchange) | Cable Landing Station | NSW | -33.8847 | 151.2265 | Telstra |  | Telstra Endeavour (2008, Sydney–Hawaii), AJC PoP | Telstra's inner-city landing/backhaul node; direct to Pitt St / Kent St exchanges. | Telstra的市内登陆/回传节点，承接Telstra Endeavour（2008年，悉尼–夏威夷）和AJC PoP，直连Pitt St / Kent St交换局。 | TeleGeography Submarine Cable Map API v3 (submarinecablemap.com/api/v3), landing-point-geo.json + country/australia.json, 2026-09-15; coordinates approximate (Telstra Paddington exchange)
CLS-BRK | Brookvale Cable Landing Station | Cable Landing Station | NSW | -33.7612 | 151.274 | Southern Cross / RTI (JGA-S) |  | Southern Cross Cable Network (2000), JGA-South (2020) | Carrier-neutral-ish northern landing for US and Guam routes; diverse from Oxford Falls. | Southern Cross（2000年）与JGA-South（2020年）的北部登陆站，承接美国和关岛路由，与Oxford Falls形成路由分散，运营商中立程度较高。 | TeleGeography Submarine Cable Map API v3 (submarinecablemap.com/api/v3), landing-point-geo.json + country/australia.json, 2026-09-15
CLS-ALX | Alexandria Cable Landing Station | Cable Landing Station | NSW | -33.9137 | 151.1962 | Southern Cross (SCCN, SC NEXT) / INDIGO-Central |  | SCCN, Southern Cross NEXT (2022), INDIGO-Central (2019) - inland CLS beside Equinix SY3/SY4 | Inland CLS embedded in the Alexandria carrier-hotel cluster - the single most important interconnection point in Australia. | 位于Alexandria运营商中立机房集群内的内陆登陆站（SCCN、Southern Cross NEXT 2022年、INDIGO-Central 2019年），紧邻Equinix SY3/SY4，是全澳最重要的互联节点。 | TeleGeography Submarine Cable Map API v3 (submarinecablemap.com/api/v3), landing-point-geo.json + country/australia.json, 2026-09-15
CLS-SYD | Sydney northern beaches (Cromer/Collaroy) landing - PPC-1, Hawaiki, CS2, Gondwana-1 | Cable Landing Station | NSW | -33.733 | 151.279 | Vocus (PPC-1), Hawaiki, Coral Sea Cable Co, OPT (Gondwana-1) |  | PPC-1 (2009), Hawaiki (2018), Coral Sea Cable (2020), Gondwana-1 (2008); planned Tabua, APX East, Hawaiki Nui, Honomoana, SMAP | Cluster of Pacific/Guam/Noumea landings; TeleGeography lumps these under 'Sydney' - exact CLS buildings vary. | Cromer / Collaroy一带的太平洋/关岛/Noumea海缆登陆集群（PPC-1、Hawaiki、Coral Sea Cable、Gondwana-1，另有Tabua、APX East、Hawaiki Nui、Honomoana、SMAP规划中），TeleGeography统一标注为“Sydney”，具体登陆站建筑各异。 | TeleGeography Submarine Cable Map API v3 (submarinecablemap.com/api/v3), landing-point-geo.json + country/australia.json, 2026-09-15; position approximate (Cromer beach manhole area)
CLS-CLV | Clovelly / Maroubra beach landings (planned SX-TX, SMAP) | Cable Landing Station | NSW | -33.94 | 151.26 | Southern Cross (SX Tasman Express 2028), SUBCO (SMAP 2026) |  | Planned/under-construction: SMAP (Sydney–Melbourne–Adelaide–Perth) at Maroubra; SX-TX at Clovelly | New eastern-suburbs landings that will terminate in the Alexandria/Mascot DC cluster. | 悉尼东郊新增登陆点：SMAP（悉尼–墨尔本–阿德莱德–珀斯，2026年）在Maroubra，SX Tasman Express（2028年）在Clovelly，均将终接于Alexandria / Mascot数据中心集群。 | TeleGeography Submarine Cable Map API v3 (submarinecablemap.com/api/v3), landing-point-geo.json + country/australia.json, 2026-09-15; position approximate (between Clovelly and Maroubra)
CLS-PER | Perth cable landing area (Floreat / City Beach; CLS Shenton Park & Floreat) | Cable Landing Station | WA | -31.94 | 115.756 | Vocus (ASC), SUBCO (OAC, SMAP), INDIGO consortium (Telstra/Singtel/Google/AARNet/Indosat/SubPartners) |  | ASC (2018), INDIGO-West & Central (2019), Oman Australia Cable (2022), SMAP (2026); TeleGeography 'Perth' point | Perth's landing cluster makes it Australia's gateway to Asia/Middle East; Equinix PE2 (Shenton Park) is adjacent. | Floreat / City Beach登陆集群（ASC 2018年、INDIGO-West与Central 2019年、Oman Australia Cable 2022年、SMAP 2026年）使珀斯成为澳洲通往亚洲和中东的门户，Equinix PE2（Shenton Park）紧邻。 | TeleGeography Submarine Cable Map API v3 (submarinecablemap.com/api/v3), landing-point-geo.json + country/australia.json, 2026-09-15; beach position approximate
CLS-PHE | Port Hedland Cable Landing Station | Cable Landing Station | WA | -20.3135 | 118.5772 | Vocus |  | North-West Cable System (2016), Darwin-Jakarta-Singapore Cable (2023) | Pilbara landing feeding NEXTDC PH1/NE1 and Asian routes via Indonesia. | Pilbara登陆站，承接North-West Cable System（2016年）和Darwin-Jakarta-Singapore Cable（2023年），供给NEXTDC PH1/NE1并经印尼接入亚洲路由。 | TeleGeography Submarine Cable Map API v3 (submarinecablemap.com/api/v3), landing-point-geo.json + country/australia.json, 2026-09-15
CLS-DRW | Darwin Cable Landing Station | Cable Landing Station | NT | -12.4675 | 130.8432 | Vocus (NWCS); planned ACC-1, Bosun, Hawaiki Nui, Project Waterworth |  | NWCS (2016); planned ACC-1 (2029), Bosun (2029), Hawaiki Nui 1 (2027), Waterworth | Darwin is being positioned as a northern subsea hub; drives the Darwin/Middle Arm DC pipeline. | 达尔文登陆站现有NWCS（2016年），规划中的ACC-1、Bosun（2029年）、Hawaiki Nui 1（2027年）和Project Waterworth将使达尔文成为北部海缆枢纽，推动达尔文 / Middle Arm数据中心管线。 | TeleGeography Submarine Cable Map API v3 (submarinecablemap.com/api/v3), landing-point-geo.json + country/australia.json, 2026-09-15
CLS-MAR | Maroochydore Cable Landing Station | Cable Landing Station | QLD | -26.6518 | 153.0894 | Sunshine Coast Council / RTI (JGA-S) |  | JGA-South (2020); planned Tabua (2026) | Queensland's only international landing; feeds NEXTDC SC1/SC2 and Brisbane via terrestrial fibre. | 昆州唯一的国际海缆登陆站（JGA-South 2020年，Tabua规划2026年），供给NEXTDC SC1/SC2，并经陆地光纤回传布里斯班。 | TeleGeography Submarine Cable Map API v3 (submarinecablemap.com/api/v3), landing-point-geo.json + country/australia.json, 2026-09-15
CLS-TQY | Torquay landing (SMAP - Melbourne) | Cable Landing Station | VIC | -38.33 | 144.326 | SUBCO |  | SMAP (2026) Melbourne landing; planned Honomoana / TalayLink / Tasman Ring at 'Melbourne' | First international-grade landing for Melbourne, giving Victorian DCs diverse routes to Sydney/Perth. | 墨尔本首个国际级海缆登陆点（SMAP 2026年，另有Honomoana / TalayLink / Tasman Ring规划中），使维州数据中心获得通往悉尼和珀斯的分散路由。 | TeleGeography Submarine Cable Map API v3 (submarinecablemap.com/api/v3), landing-point-geo.json + country/australia.json, 2026-09-15; position approximate
CLS-4MB | Four Mile Bluff Cable Landing (Basslink fibre) | Cable Landing Station | TAS | -41.0333 | 146.8502 | APA (Basslink) / planned Bernacchi-1 |  | Basslink fibre (2005); Bernacchi-1 (2027 planned) | Tasmania's main fibre link to the mainland; critical for Bell Bay DC proposals. | 塔州连接大陆的主光纤通道（Basslink光纤2005年，Bernacchi-1规划2027年），Bell Bay数据中心提案的关键前提。 | TeleGeography Submarine Cable Map API v3 (submarinecablemap.com/api/v3), landing-point-geo.json + country/australia.json, 2026-09-15
CLS-STN | Stanley / Boat Harbour landings (Bass Strait-1 & -2) | Cable Landing Station | TAS | -40.7604 | 145.2941 | Telstra |  | Bass Strait-1 (Boat Harbour–Sandy Point, 1995), Bass Strait-2 (Stanley–Inverloch, 2003) | Telstra's two Bass Strait cables; provide diversity from Basslink for Tasmanian DCs. | Telstra的两条Bass Strait海缆（Bass Strait-1 Boat Harbour–Sandy Point 1995年、Bass Strait-2 Stanley–Inverloch 2003年），为塔州数据中心提供Basslink以外的路由分散。 | TeleGeography Submarine Cable Map API v3 (submarinecablemap.com/api/v3), landing-point-geo.json + country/australia.json, 2026-09-15
IX-SY1 | Equinix SY1/SY2 - 639 Gardeners Rd, Mascot | Internet Exchange / Carrier Hotel | NSW | -33.9219 | 151.188 | Equinix |  | Original Sydney carrier hotel; NSW-IX SYD1, Equinix IX, Megaport | Australia's most connected building - 200+ carriers, IX and cloud on-ramps. | 澳洲互联程度最高的建筑，悉尼最早的运营商中立机房，汇集200多家运营商、NSW-IX SYD1、Equinix IX、Megaport及各云商接入点。 | IX Australia PoP list (ix.asn.au/services/peering) + Megaport public locations API (api.megaport.com/v2/locations); coordinates geocoded from street address
IX-SY3 | Equinix SY3 - 47 Bourke Rd, Alexandria | Internet Exchange / Carrier Hotel | NSW | -33.9122 | 151.1938 | Equinix |  | NSW-IX SYD3; Megaport; Southern Cross / INDIGO cable PoP | Cable-system PoP and hyperscaler on-ramp hub for Alexandria campus. | Alexandria园区的海缆PoP（Southern Cross / INDIGO）和超大规模云商接入枢纽，设有NSW-IX SYD3和Megaport。 | IX Australia PoP list (ix.asn.au/services/peering) + Megaport public locations API (api.megaport.com/v2/locations); coordinates geocoded from street address
IX-SY4 | Equinix SY4/SY5 - 200 Bourke Rd, Alexandria | Internet Exchange / Carrier Hotel | NSW | -33.9165 | 151.1948 | Equinix |  | NSW-IX PoP; AWS/Azure/Google on-ramps | Newest Equinix Alexandria buildings; extends the SY3 interconnection fabric. | Equinix在Alexandria最新的两座机房，延伸SY3的互联架构，设有NSW-IX PoP及AWS / Azure / Google接入点。 | IX Australia PoP list (ix.asn.au/services/peering) + Megaport public locations API (api.megaport.com/v2/locations); coordinates geocoded from street address; coordinates approximate
IX-GSW | DigiCo SYD1 (ex Global Switch) - 400 Harris St, Ultimo | Internet Exchange / Carrier Hotel | NSW | -33.8755 | 151.1978 | DigiCo Infrastructure REIT |  | ~40 MW; NSW-IX SYD2; Megaport | Sydney CBD-fringe carrier hotel, second-largest interconnection point after Mascot. | 悉尼CBD边缘的运营商中立机房（约40 MW，原Global Switch），互联规模仅次于Mascot，设有NSW-IX SYD2和Megaport。 | IX Australia PoP list (ix.asn.au/services/peering) + Megaport public locations API (api.megaport.com/v2/locations); coordinates geocoded from street address
IX-S1 | NEXTDC S1 - 4 Eden Park Dr, Macquarie Park | Internet Exchange / Carrier Hotel | NSW | -33.7851 | 151.1312 | NEXTDC |  | 16 MW; NSW-IX SYD4; Megaport | Anchor of the Macquarie Park cluster; NEXTDC's original Sydney site. | NEXTDC最早的悉尼站点（16 MW），Macquarie Park集群的锚点，设有NSW-IX SYD4和Megaport。 | IX Australia PoP list (ix.asn.au/services/peering) + Megaport public locations API (api.megaport.com/v2/locations); coordinates geocoded from street address
IX-S2 | NEXTDC S2 - 6-8 Giffnock Ave, Macquarie Park | Internet Exchange / Carrier Hotel | NSW | -33.783 | 151.124 | NEXTDC |  | 30 MW; NSW-IX SYD7 | Large enterprise/cloud site adjacent to S1; part of the S1/S2/S5 campus. | 紧邻S1的大型企业/云站点（30 MW，NSW-IX SYD7），与S1、S5构成同一园区。 | IX Australia PoP list (ix.asn.au/services/peering) + Megaport public locations API (api.megaport.com/v2/locations); coordinates geocoded from street address; coordinates approximate
IX-MQT | Macquarie Telecom Intellicentre 2/3 - 17-23 Talavera Rd, Macquarie Park | Internet Exchange / Carrier Hotel | NSW | -33.7772 | 151.123 | Macquarie Data Centres |  | IC2 + IC3 East (~50 MW planned); NSW-IX PoP; government-certified | Sovereign/government cloud hub in Macquarie Park. | Macquarie Park的主权/政府云枢纽，IC2加IC3 East规划约50 MW，持政府认证，设有NSW-IX PoP。 | IX Australia PoP list (ix.asn.au/services/peering) + Megaport public locations API (api.megaport.com/v2/locations); coordinates geocoded from street address; coordinates approximate
IX-ME1 | Equinix ME1 - 578 Lorimer St, Port Melbourne | Internet Exchange / Carrier Hotel | VIC | -37.8227 | 144.9285 | Equinix |  | VIC-IX MEL4; Equinix IX; Megaport | Melbourne's primary carrier hotel and IX site. | 墨尔本首要的运营商中立机房和IX站点，设有VIC-IX MEL4、Equinix IX及Megaport。 | IX Australia PoP list (ix.asn.au/services/peering) + Megaport public locations API (api.megaport.com/v2/locations); coordinates geocoded from street address; coordinates approximate
IX-M1 | NEXTDC M1 - 826 Lorimer St, Port Melbourne | Internet Exchange / Carrier Hotel | VIC | -37.822 | 144.9324 | NEXTDC |  | 16 MW; VIC-IX MEL3; Megaport | Highly connected Port Melbourne site next to Equinix ME1; M4 (150 MW) adjacent. | Port Melbourne互联度极高的站点（16 MW，VIC-IX MEL3、Megaport），紧邻Equinix ME1，M4（150 MW）在旁。 | IX Australia PoP list (ix.asn.au/services/peering) + Megaport public locations API (api.megaport.com/v2/locations); coordinates geocoded from street address
IX-530 | 530 Collins St (Vocus VDC-MEL03 / MelbDC) | Internet Exchange / Carrier Hotel | VIC | -37.8182 | 144.956 | Vocus / MelbDC |  | VIC-IX MEL5 (Vocus L3) and MelbDC L15 | Melbourne CBD carrier-neutral meet-me point. | 墨尔本CBD的运营商中立交汇点，VIC-IX MEL5（Vocus 3层）与MelbDC（15层）设于此。 | IX Australia PoP list (ix.asn.au/services/peering) + Megaport public locations API (api.megaport.com/v2/locations); coordinates geocoded from street address; coordinates approximate
IX-B1 | NEXTDC B1 - 20 Wharf St, Brisbane | Internet Exchange / Carrier Hotel | QLD | -27.4655 | 153.0296 | NEXTDC |  | 2.25 MW; QLD-IX BNE1; Megaport | Brisbane CBD's key carrier-neutral interconnection site. | 布里斯班CBD的核心运营商中立互联站点（2.25 MW，QLD-IX BNE1、Megaport）。 | IX Australia PoP list (ix.asn.au/services/peering) + Megaport public locations API (api.megaport.com/v2/locations); coordinates geocoded from street address
IX-B2 | NEXTDC B2 - 454 St Pauls Tce, Fortitude Valley | Internet Exchange / Carrier Hotel | QLD | -27.4535 | 153.0335 | NEXTDC |  | 12 MW; QLD-IX BNE6 | Largest carrier-neutral facility in inner Brisbane. | 布里斯班内城最大的运营商中立机房（12 MW，QLD-IX BNE6）。 | IX Australia PoP list (ix.asn.au/services/peering) + Megaport public locations API (api.megaport.com/v2/locations); coordinates geocoded from street address; coordinates approximate
IX-P2 | NEXTDC P2 - 11 Newcastle St, Perth | Internet Exchange / Carrier Hotel | WA | -31.947 | 115.8595 | NEXTDC |  | 20+ MW; WA-IX PER3 | Perth CBD interconnection hub for subsea-cable backhaul. | 珀斯CBD的互联枢纽（20 MW以上，WA-IX PER3），承接海缆回传。 | IX Australia PoP list (ix.asn.au/services/peering) + Megaport public locations API (api.megaport.com/v2/locations); coordinates geocoded from street address; coordinates approximate
IX-PE2 | Equinix PE2 - 37 Lemnos St, Shenton Park | Internet Exchange / Carrier Hotel | WA | -31.9575 | 115.8005 | Equinix |  | WA-IX PER4; Equinix IX; cable-system PoP (INDIGO/ASC/OAC) | Perth's cable-landing-adjacent carrier hotel. | 紧邻珀斯海缆登陆区的运营商中立机房，设有WA-IX PER4、Equinix IX及INDIGO / ASC / OAC海缆PoP。 | IX Australia PoP list (ix.asn.au/services/peering) + Megaport public locations API (api.megaport.com/v2/locations); coordinates geocoded from street address; coordinates approximate
IX-VPE | Vocus VDC-PER01 - 1 William St (QV1), Perth | Internet Exchange / Carrier Hotel | WA | -31.9535 | 115.8582 | Vocus |  | WA-IX PER2 | Vocus's Perth CBD hub and ASC cable backhaul terminus. | Vocus的珀斯CBD枢纽（WA-IX PER2），ASC海缆回传的终点。 | IX Australia PoP list (ix.asn.au/services/peering) + Megaport public locations API (api.megaport.com/v2/locations); coordinates geocoded from street address; coordinates approximate
IX-A1 | NEXTDC A1 - 125 Frome St, Adelaide | Internet Exchange / Carrier Hotel | SA | -34.927 | 138.6085 | NEXTDC |  | 5 MW; SA-IX ADL1 | Adelaide's main carrier-neutral DC and IX site. | 阿德莱德主要的运营商中立数据中心和IX站点（5 MW，SA-IX ADL1）。 | IX Australia PoP list (ix.asn.au/services/peering) + Megaport public locations API (api.megaport.com/v2/locations); coordinates geocoded from street address; coordinates approximate
IX-C1 | NEXTDC C1 - 19 Battye St, Bruce | Internet Exchange / Carrier Hotel | ACT | -35.245 | 149.093 | NEXTDC |  | 4.4 MW; ACT-IX CBR1 | Canberra's key carrier-neutral/government interconnection site. | 堪培拉的核心运营商中立/政府互联站点（4.4 MW，ACT-IX CBR1）。 | IX Australia PoP list (ix.asn.au/services/peering) + Megaport public locations API (api.megaport.com/v2/locations); coordinates geocoded from street address; coordinates approximate
TX-PITT | Telstra Pitt Street / Castlereagh St Exchange (City South) | Telstra Exchange (major) | NSW | -33.8757 | 151.2086 | Telstra |  | Sydney's principal switching centre; NBN POI 2CYS (City South) in same complex | Historic core of Australian telecoms; most carriers' Sydney trunk fibre terminates here. | 澳洲电信网络的历史核心和悉尼主交换中心，多数运营商的悉尼干线光纤在此终接，NBN POI 2CYS（City South）位于同一楼群。 | Community/press knowledge of Telstra exchange sites; coordinates from NBN POI list (same building) or geocoded street address. Verify against GA Telephone_Exchanges MapServer
TX-DALL | Telstra Dalley Street Exchange | Telstra Exchange (major) | NSW | -33.8629 | 151.2083 | Telstra |  | 6-10 Underwood St; NBN POI 2DAL | Northern CBD exchange; international gateway heritage (OTC), dense carrier presence. | 悉尼CBD北部的交换局（6-10 Underwood St，NBN POI 2DAL），前身为OTC国际网关，运营商密集。 | Community/press knowledge of Telstra exchange sites; coordinates from NBN POI list (same building) or geocoded street address. Verify against GA Telephone_Exchanges MapServer
TX-KENT | Telstra Kent Street Exchange | Telstra Exchange (major) | NSW | -33.8712 | 151.2048 | Telstra |  | Major CBD exchange, Kent St (west CBD) | Second CBD switching node used for diverse trunk routing to Pitt St. | 悉尼CBD西侧的主要交换局，Pitt St之外的第二切换节点，用于干线的分散路由。 | Community/press knowledge of Telstra exchange sites; coordinates from NBN POI list (same building) or geocoded street address. Verify against GA Telephone_Exchanges MapServer; coordinates approximate
TX-EXHB | Telstra Exhibition Street Exchange | Telstra Exchange (major) | VIC | -37.8087 | 144.9697 | Telstra |  | 300 Exhibition St; NBN POI 3EXH; Telstra HQ precinct | Melbourne's principal exchange and carrier meet-point. | 墨尔本首要的交换局和运营商交汇点（300 Exhibition St，NBN POI 3EXH，Telstra总部园区）。 | Community/press knowledge of Telstra exchange sites; coordinates from NBN POI list (same building) or geocoded street address. Verify against GA Telephone_Exchanges MapServer
TX-LONS | Telstra Lonsdale Street Exchange | Telstra Exchange (major) | VIC | -37.8125 | 144.9595 | Telstra |  | Lonsdale St, Melbourne CBD | Second CBD exchange giving diverse routing to Exhibition St. | 墨尔本CBD的第二交换局，与Exhibition St形成分散路由。 | Community/press knowledge of Telstra exchange sites; coordinates from NBN POI list (same building) or geocoded street address. Verify against GA Telephone_Exchanges MapServer; coordinates approximate
TX-EDIS | Telstra Edison Exchange - Edward St, Brisbane | Telstra Exchange (major) | QLD | -27.4665 | 153.028 | Telstra |  | Brisbane CBD principal exchange | Brisbane's core switching node; backhaul point for QLD regional fibre. | 布里斯班CBD的主交换局和核心切换节点，昆州区域光纤在此回传。 | Community/press knowledge of Telstra exchange sites; coordinates from NBN POI list (same building) or geocoded street address. Verify against GA Telephone_Exchanges MapServer; coordinates approximate
TX-WELL | Telstra Wellington Street Exchange, Perth | Telstra Exchange (major) | WA | -31.9518 | 115.863 | Telstra |  | Perth CBD principal exchange | Perth's core exchange; terrestrial backhaul for subsea cables to the east coast. | 珀斯CBD的主交换局和核心切换节点，承接海缆至东海岸的陆地回传。 | Community/press knowledge of Telstra exchange sites; coordinates from NBN POI list (same building) or geocoded street address. Verify against GA Telephone_Exchanges MapServer; coordinates approximate
TX-WAYM | Telstra Waymouth Street Exchange, Adelaide | Telstra Exchange (major) | SA | -34.9255 | 138.5975 | Telstra |  | Adelaide CBD principal exchange | Adelaide's core switching node. | 阿德莱德CBD的主交换局和核心切换节点。 | Community/press knowledge of Telstra exchange sites; coordinates from NBN POI list (same building) or geocoded street address. Verify against GA Telephone_Exchanges MapServer; coordinates approximate
TX-CIVC | Telstra Civic Exchange - 50 Mort St, Braddon | Telstra Exchange (major) | ACT | -35.2738 | 149.1316 | Telstra |  | NBN POI 9CVI | Canberra's principal exchange serving government networks. | 堪培拉的主交换局（NBN POI 9CVI），服务政府网络。 | Community/press knowledge of Telstra exchange sites; coordinates from NBN POI list (same building) or geocoded street address. Verify against GA Telephone_Exchanges MapServer
TX-HOBA | Telstra Hobart Exchange - 2 Heathfield Ave | Telstra Exchange (major) | TAS | -42.8868 | 147.3272 | Telstra |  | NBN POI 7HOB; TAS-IX HBA1 | Hobart's core exchange and IX location. | 霍巴特的核心交换局，NBN POI 7HOB与TAS-IX HBA1所在地。 | Community/press knowledge of Telstra exchange sites; coordinates from NBN POI list (same building) or geocoded street address. Verify against GA Telephone_Exchanges MapServer
POI-2SYB | NBN POI 2SYB - Eastern Creek Depot | NBN POI | NSW | -33.8143 | 150.8361 | NBN Co |  | POI ID 2SYB | Largest western-Sydney aggregation POI, 6 Roberts Rd - co-located with the Eastern Creek DC cluster. | 西悉尼最大的NBN汇聚POI（6 Roberts Rd），与Eastern Creek数据中心集群共址。 | NBN POI list (gist.github.com/dleonard0/27a707e149d061ed0a1d18009e485e77 - community dataset used by nbn.rinseout.org); POI IDs cross-checked on nbn.rinseout.org state pages
POI-2SYA | NBN POI 2SYA - Asquith Depot | NBN POI | NSW | -33.6957 | 151.1099 | NBN Co |  | POI ID 2SYA | Northern Sydney aggregation POI. | 北悉尼的NBN汇聚POI。 | NBN POI list (gist.github.com/dleonard0/27a707e149d061ed0a1d18009e485e77 - community dataset used by nbn.rinseout.org); POI IDs cross-checked on nbn.rinseout.org state pages
POI-2CHA | NBN POI 2CHA - Chatswood | NBN POI | NSW | -33.7976 | 151.1805 | NBN Co |  | POI ID 2CHA | Serves lower north shore incl. Artarmon/St Leonards DC zone. | 覆盖悉尼下北岸的NBN POI，含Artarmon / St Leonards数据中心片区。 | NBN POI list (gist.github.com/dleonard0/27a707e149d061ed0a1d18009e485e77 - community dataset used by nbn.rinseout.org); POI IDs cross-checked on nbn.rinseout.org state pages
POI-2PAR | NBN POI 2PAR - Parramatta | NBN POI | NSW | -33.814 | 151.0024 | NBN Co |  | POI ID 2PAR | Central-west Sydney POI. | 悉尼中西部的NBN POI。 | NBN POI list (gist.github.com/dleonard0/27a707e149d061ed0a1d18009e485e77 - community dataset used by nbn.rinseout.org); POI IDs cross-checked on nbn.rinseout.org state pages
POI-2LIV | NBN POI 2LIV - Liverpool | NBN POI | NSW | -33.926 | 150.9241 | NBN Co |  | POI ID 2LIV | South-west Sydney POI near Moorebank/Prestons DC land. | 悉尼西南的NBN POI，邻近Moorebank / Prestons数据中心用地。 | NBN POI list (gist.github.com/dleonard0/27a707e149d061ed0a1d18009e485e77 - community dataset used by nbn.rinseout.org); POI IDs cross-checked on nbn.rinseout.org state pages
POI-2BLK | NBN POI 2BLK - Blacktown | NBN POI | NSW | -33.7703 | 150.9083 | NBN Co |  | POI ID 2BLK | Western Sydney POI. | 西悉尼的NBN POI。 | NBN POI list (gist.github.com/dleonard0/27a707e149d061ed0a1d18009e485e77 - community dataset used by nbn.rinseout.org); POI IDs cross-checked on nbn.rinseout.org state pages
POI-2KNS | NBN POI 2KNS - Kensington | NBN POI | NSW | -33.9102 | 151.2203 | NBN Co |  | POI ID 2KNS | Eastern suburbs POI near Alexandria/Mascot cluster. | 悉尼东郊的NBN POI，邻近Alexandria / Mascot集群。 | NBN POI list (gist.github.com/dleonard0/27a707e149d061ed0a1d18009e485e77 - community dataset used by nbn.rinseout.org); POI IDs cross-checked on nbn.rinseout.org state pages
POI-3MEB | NBN POI 3MEB - Port Melbourne Depot | NBN POI | VIC | -37.8257 | 144.9055 | NBN Co |  | POI ID 3MEB | Melbourne aggregation POI beside Equinix ME1 / NEXTDC M1. | 墨尔本的NBN汇聚POI，紧邻Equinix ME1 / NEXTDC M1。 | NBN POI list (gist.github.com/dleonard0/27a707e149d061ed0a1d18009e485e77 - community dataset used by nbn.rinseout.org); POI IDs cross-checked on nbn.rinseout.org state pages
POI-3MEA | NBN POI 3MEA - Nunawading Depot | NBN POI | VIC | -37.8212 | 145.167 | NBN Co |  | POI ID 3MEA | Eastern Melbourne aggregation POI. | 墨尔本东部的NBN汇聚POI。 | NBN POI list (gist.github.com/dleonard0/27a707e149d061ed0a1d18009e485e77 - community dataset used by nbn.rinseout.org); POI IDs cross-checked on nbn.rinseout.org state pages
POI-3FSR | NBN POI 3FSR - Footscray | NBN POI | VIC | -37.8029 | 144.8994 | NBN Co |  | POI ID 3FSR | Inner-west POI near NEXTDC M3. | 墨尔本内西区的NBN POI，邻近NEXTDC M3。 | NBN POI list (gist.github.com/dleonard0/27a707e149d061ed0a1d18009e485e77 - community dataset used by nbn.rinseout.org); POI IDs cross-checked on nbn.rinseout.org state pages
POI-3TMN | NBN POI 3TMN - Tullamarine | NBN POI | VIC | -37.7051 | 144.8836 | NBN Co |  | POI ID 3TMN | Airport-precinct POI near NEXTDC M2 / AirTrunk MEL1. | 机场片区的NBN POI，邻近NEXTDC M2 / AirTrunk MEL1。 | NBN POI list (gist.github.com/dleonard0/27a707e149d061ed0a1d18009e485e77 - community dataset used by nbn.rinseout.org); POI IDs cross-checked on nbn.rinseout.org state pages
POI-3DAD | NBN POI 3DAD - Dandenong | NBN POI | VIC | -37.987 | 145.2161 | NBN Co |  | POI ID 3DAD | South-east Melbourne POI. | 墨尔本东南部的NBN POI。 | NBN POI list (gist.github.com/dleonard0/27a707e149d061ed0a1d18009e485e77 - community dataset used by nbn.rinseout.org); POI IDs cross-checked on nbn.rinseout.org state pages
POI-4WOB | NBN POI 4WOB - Woolloongabba | NBN POI | QLD | -27.484 | 153.0365 | NBN Co |  | POI ID 4WOB | Brisbane inner-south POI. | 布里斯班内南区的NBN POI。 | NBN POI list (gist.github.com/dleonard0/27a707e149d061ed0a1d18009e485e77 - community dataset used by nbn.rinseout.org); POI IDs cross-checked on nbn.rinseout.org state pages
POI-4BNB | NBN POI 4BNB - Aspley Depot | NBN POI | QLD | -27.3548 | 153.0288 | NBN Co |  | POI ID 4BNB | Northern Brisbane aggregation POI. | 布里斯班北部的NBN汇聚POI。 | NBN POI list (gist.github.com/dleonard0/27a707e149d061ed0a1d18009e485e77 - community dataset used by nbn.rinseout.org); POI IDs cross-checked on nbn.rinseout.org state pages
POI-4BNA | NBN POI 4BNA - Acacia Ridge Depot | NBN POI | QLD | -27.5973 | 153.0366 | NBN Co |  | POI ID 4BNA | Southern Brisbane aggregation POI near Rocklea. | 布里斯班南部的NBN汇聚POI，邻近Rocklea。 | NBN POI list (gist.github.com/dleonard0/27a707e149d061ed0a1d18009e485e77 - community dataset used by nbn.rinseout.org); POI IDs cross-checked on nbn.rinseout.org state pages
POI-6PEB | NBN POI 6PEB - Bentley Depot | NBN POI | WA | -31.9995 | 115.9249 | NBN Co |  | POI ID 6PEB | Perth aggregation POI. | 珀斯的NBN汇聚POI。 | NBN POI list (gist.github.com/dleonard0/27a707e149d061ed0a1d18009e485e77 - community dataset used by nbn.rinseout.org); POI IDs cross-checked on nbn.rinseout.org state pages
POI-6PEA | NBN POI 6PEA - Wangara Depot | NBN POI | WA | -31.7918 | 115.8453 | NBN Co |  | POI ID 6PEA | Northern Perth aggregation POI near NEXTDC P1. | 珀斯北部的NBN汇聚POI，邻近NEXTDC P1。 | NBN POI list (gist.github.com/dleonard0/27a707e149d061ed0a1d18009e485e77 - community dataset used by nbn.rinseout.org); POI IDs cross-checked on nbn.rinseout.org state pages
POI-6SUB | NBN POI 6SUB - Subiaco | NBN POI | WA | -31.9498 | 115.8244 | NBN Co |  | POI ID 6SUB | Inner Perth POI near Shenton Park cable PoPs. | 珀斯内城的NBN POI，邻近Shenton Park海缆PoP。 | NBN POI list (gist.github.com/dleonard0/27a707e149d061ed0a1d18009e485e77 - community dataset used by nbn.rinseout.org); POI IDs cross-checked on nbn.rinseout.org state pages
POI-5ADB | NBN POI 5ADB - Greenfields Depot | NBN POI | SA | -34.7933 | 138.6034 | NBN Co |  | POI ID 5ADB | Northern Adelaide aggregation POI. | 阿德莱德北部的NBN汇聚POI。 | NBN POI list (gist.github.com/dleonard0/27a707e149d061ed0a1d18009e485e77 - community dataset used by nbn.rinseout.org); POI IDs cross-checked on nbn.rinseout.org state pages
POI-5ADA | NBN POI 5ADA - Lonsdale Depot | NBN POI | SA | -35.1164 | 138.4996 | NBN Co |  | POI ID 5ADA | Southern Adelaide aggregation POI. | 阿德莱德南部的NBN汇聚POI。 | NBN POI list (gist.github.com/dleonard0/27a707e149d061ed0a1d18009e485e77 - community dataset used by nbn.rinseout.org); POI IDs cross-checked on nbn.rinseout.org state pages
POI-8DRW | NBN POI 8DRW - Darwin | NBN POI | NT | -12.4586 | 130.8365 | NBN Co |  | POI ID 8DRW | Sole NT POI, 99 Smith St. | 北领地唯一的NBN POI（99 Smith St）。 | NBN POI list (gist.github.com/dleonard0/27a707e149d061ed0a1d18009e485e77 - community dataset used by nbn.rinseout.org); POI IDs cross-checked on nbn.rinseout.org state pages

## NBN_POI
poi_id | name | state | lat | lng | address | source
9CVI | Civic | ACT | -35.2738 | 149.1316 | 50 Mort Street, Braddon ACT 2612 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
9QBN | Queanbeyan | NSW | -35.3536 | 149.2319 | 36 Lowe St, Queanbeyan NSW 2620 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2ALB | Albury | NSW | -36.0819 | 146.9149 | 475 Kiewa St, Albury NSW 2640 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2SYA | Asquith Depot | NSW | -33.6957 | 151.1099 | 3 Kelray Place, Asquith NSW 2077 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2BLV | Berkeley Vale | NSW | -33.3491 | 151.436 | 3-5 Pindarri Ave, Berkeley Vale NSW 2261 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2BLK | Blacktown | NSW | -33.7703 | 150.9083 | 17 Flushcombe Rd, Blacktown NSW 2148 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2CBT | Campbelltown | NSW | -34.068 | 150.8119 | 253 Queen St, Campbelltown NSW 2560 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2CAM | Campsie | NSW | -33.9159 | 151.1095 | 395 Canterbury Rd, Campsie NSW 2194 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2CRR | Carramar | NSW | -33.8882 | 150.9689 | 6-12 The Horsley Dr, Carramar NSW 2163 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2CAS | Castle Hill | NSW | -33.732 | 151.0051 | 4 Castle Pl, Castle Hill NSW 2154 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2CHA | Chatswood | NSW | -33.7976 | 151.1805 | 1 Thomas St, Chatswood NSW 2067 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2CYS | City South | NSW | -33.8757 | 151.2086 | 225 Castlereagh St, Sydney NSW 2000 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2CFS | Coffs Harbour | NSW | -30.2965 | 153.1132 | 3 Moonee St, Coffs Harbour NSW 2450 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2DAL | Dalley | NSW | -33.8629 | 151.2083 | 6-10 Underwood St (cnr Dalley St), Sydney NSW 2000 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2DBB | Dubbo | NSW | -32.2463 | 148.602 | 100 Macquarie St, Dubbo NSW 2830 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2SYB | Eastern Creek Depot | NSW | -33.8143 | 150.8361 | 6 Roberts Road, Eastern Creek NSW 2766 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2EDG | Edgecliff | NSW | -33.8795 | 151.2385 | 295 New South Head Rd, Edgecliff NSW 2027 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2FRE | Frenchs Forest | NSW | -33.7523 | 151.225 | 510 Warringah Rd, Frenchs Forest NSW 2086 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2GBE | Glebe | NSW | -33.8807 | 151.1885 | 120-126 St Johns Rd, Glebe NSW 2037 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2GOS | Gosford | NSW | -33.43 | 151.3415 | 21-23 Mann St, Gosford NSW 2250 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2GRN | Grafton | NSW | -29.691 | 152.934 | 131 Pound St, Grafton NSW 2460 (NOTE: source gist had wrong Newcastle coords; corrected to approx Grafton exchange) | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2HAM | Hamilton | NSW | -32.926 | 151.7486 | 117 Lawson St, Hamilton NSW 2303 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2KNS | Kensington | NSW | -33.9102 | 151.2203 | 115 Todman Ave, Kensington NSW 2033 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2LAK | Lakemba | NSW | -33.9207 | 151.0762 | 18 Croydon Rd, Lakemba NSW 2195 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2LID | Lidcombe | NSW | -33.8647 | 151.0441 | 1 Taylor St, Lidcombe NSW 2141 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2LIV | Liverpool | NSW | -33.926 | 150.9241 | 40 Terminus St, Liverpool NSW 2170 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2MAI | Maitland | NSW | -32.7499 | 151.5869 | 123 George St, East Maitland NSW 2323 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2MYF | Mayfield | NSW | -32.8964 | 151.7349 | 314 Maitland Rd, Mayfield NSW 2304 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2MIR | Miranda | NSW | -34.0344 | 151.1018 | 576 Kingsway, Miranda NSW 2228 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2MOS | Mosman | NSW | -33.8292 | 151.2448 | 850 Military Rd, Mosman NSW 2088 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2NEW | Newtown | NSW | -33.8961 | 151.1792 | 2-4 Mary St, Newtown NSW 2042 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2NWR | Nowra-Bomaderry | NSW | -34.8758 | 150.6009 | 71 Worrigee St, Nowra NSW 2541 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2PAR | Parramatta | NSW | -33.814 | 151.0024 | 91-93 Marsden St, Parramatta NSW 2151 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2PEA | Peakhurst | NSW | -33.9527 | 151.0652 | 41-43 Baumans Rd, Peakhurst NSW 2210 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2PEN | Pendle Hill | NSW | -33.8047 | 150.9603 | 209 Dunmore St, Pendle Hill NSW 2145 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2PTH | Penrith | NSW | -33.7529 | 150.699 | 90-92 Henry Street, Penrith NSW 2750 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2ROC | Rockdale | NSW | -33.9484 | 151.1392 | 395-405 Princes Hwy, Rockdale NSW 2216 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2RYD | Ryde | NSW | -33.8136 | 151.1053 | 116 Blaxland Rd, Ryde NSW 2112 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2STL | St Leonards | NSW | -33.8236 | 151.196 | 524 Pacific Hwy, St Leonards NSW 2065 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2TAM | Tamworth | NSW | -31.0917 | 150.9315 | 23 Fitzroy St, Tamworth NSW 2340 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2WAG | Wagga Wagga | NSW | -35.1064 | 147.371 | 226 Tarcutta St, Wagga Wagga NSW 2650 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2WIN | Windsor | NSW | -33.6134 | 150.8128 | 22 Brabyn St, Windsor NSW 2756 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
2WLG | Wollongong | NSW | -34.4254 | 150.8899 | 296-298 Crown St, Wollongong NSW 2500 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
8DRW | Darwin | NT | -12.4586 | 130.8365 | 99 Smith St, Darwin NT 0800 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4BNA | Acacia Ridge Depot | QLD | -27.5973 | 153.0366 | 470 Bradman St, Acacia Ridge QLD 4110 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4APL | Aspley | QLD | -27.3575 | 153.0226 | 728 Zillmere Rd, Aspley QLD 4034 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4BNB | Aspley Depot | QLD | -27.3548 | 153.0288 | 16/605 Zillmere Road, Aspley QLD 4034 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4BBE | Bundaberg | QLD | -24.8659 | 152.3482 | 157 Bourbong St, Bundaberg QLD 4670 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4BDB | Bundamba | QLD | -27.6061 | 152.8183 | 2 Taylor St, Bundamba QLD 4304 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4CAB | Caboolture | QLD | -27.0854 | 152.9517 | 36 King St, Caboolture QLD 4510 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4CAI | Cairns | QLD | -16.9239 | 145.7729 | 82-86 Shields St, Cairns QLD 4870 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4CPH | Camp Hill | QLD | -27.4934 | 153.0769 | 593 Old Cleveland Rd, Camp Hill QLD 4152 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4EMP | Eight Mile | QLD | -27.5902 | 153.106 | 23 Millers Rd, Eight Mile Plains QLD 4113 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4GDN | Goodna | QLD | -27.6059 | 152.8897 | 16 Stuart St, Goodna QLD 4300 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4IPS | Ipswich | QLD | -27.6149 | 152.7611 | 76 Brisbane St, Ipswich QLD 4305 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4MKY | Mackay | QLD | -21.1395 | 149.1865 | 35 River St, Mackay QLD 4740 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4MRA | Merrimac | QLD | -28.0491 | 153.4269 | 199 Sunshine Blvd, Mermaid Waters QLD 4218 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4NBR | Nambour | QLD | -26.6278 | 152.9602 | 137-145 Currie St, Nambour QLD 4560 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4NER | Nerang | QLD | -27.9943 | 153.3437 | 31 Nerang-Broadbeach Rd, Nerang QLD 4211 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4KLG | Petrie | QLD | -27.2693 | 152.9773 | 6 Dayboro Rd, Petrie QLD 4502 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4ROT | Rockhampton | QLD | -23.3781 | 150.5127 | 12 Denham St, Rockhampton QLD 4700 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4SLA | Slacks Creek | QLD | -27.6382 | 153.1182 | 257 Kingston Rd, Logan Central QLD 4114 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4SOP | Southport | QLD | -27.9674 | 153.4138 | 41 Nerang Rd, Southport QLD 4215 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4TOB | Toowoomba | QLD | -27.5622 | 151.9568 | 157 Hume St, Toowoomba QLD 4350 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4TNS | Townsville | QLD | -19.2581 | 146.8171 | 22 Sturt St, Townsville QLD 4810 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
4WOB | Woolloongabba | QLD | -27.484 | 153.0365 | 820 Main St, Kangaroo Point QLD 4169 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
5EDW | Edwardstown | SA | -34.9619 | 138.5721 | 688 South Rd, Glandore SA 5037 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
5EZB | Elizabeth | SA | -34.7222 | 138.6685 | 24-26 Philip Hwy, Elizabeth SA 5112 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
5ADB | Greenfields Depot | SA | -34.7933 | 138.6034 | 8-12 George St, Green Fields SA 5107 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
5ADA | Lonsdale Depot | SA | -35.1164 | 138.4996 | 73 O'Sullivan Beach Road, Lonsdale SA 5160 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
5MOD | Modbury | SA | -34.8294 | 138.6872 | 130-134 Reservoir Rd, Modbury SA 5092 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
5PTA | Port Augusta | SA | -32.4911 | 137.7624 | 5 Mackay St, Port Augusta SA 5700 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
5PRO | Prospect | SA | -34.8918 | 138.6022 | 73-77 Ballville St, Prospect SA 5082 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
5CPK | St Marys | SA | -34.9918 | 138.585 | 184 Daws Rd, Daw Park SA 5041 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
5STI | Stirling | SA | -35.0066 | 138.7166 | 42 Mount Barker Road, Stirling SA 5152 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
7HOB | Hobart | TAS | -42.8868 | 147.3272 | 2 Heathfield Ave, Hobart TAS 7000 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
7LAU | Launceston | TAS | -41.4351 | 147.1374 | 51 St John St, Launceston TAS 7250 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3BRA | Ballarat | VIC | -37.5649 | 143.8546 | 105-111 Doveton St S, Ballarat VIC 3350 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3BEN | Bendigo | VIC | -36.7615 | 144.2762 | 38 Short St, Bendigo VIC 3550 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3CAU | Caulfield | VIC | -37.876 | 145.0468 | 78 Waverley Rd, Caulfield VIC 3145 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3CTA | Cheltenham | VIC | -37.9643 | 145.0555 | 315 Charman Rd, Cheltenham VIC 3192 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3CBN | Cranbourne | VIC | -38.1042 | 145.2827 | 196 High St, Cranbourne VIC 3977 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3DAD | Dandenong | VIC | -37.987 | 145.2161 | 149 Walker Street, Dandenong VIC 3175 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3EXH | Exhibition | VIC | -37.8087 | 144.9697 | 5/300 Exhibition St, Melbourne VIC 3000 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3FSR | Footscray | VIC | -37.8029 | 144.8994 | 82 Napier St, Footscray VIC 3011 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3GEE | Geelong | VIC | -38.1491 | 144.3558 | 17-19 Little Ryrie St, Geelong VIC 3220 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3HAW | Hawthorn | VIC | -37.8222 | 145.0365 | 375 Burwood Rd, Hawthorn VIC 3122 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3HRS | Horsham | VIC | -36.7134 | 142.2002 | 25 Mclachlan St, Horsham VIC 3400 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3KAL | Karingal | VIC | -38.1534 | 145.1618 | 228 Karingal Dr, Karingal VIC 3199 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3KEW | Kew | VIC | -37.8083 | 145.0291 | 106-108 Denmark St, Kew VIC 3101 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3KEY | Keysborough | VIC | -37.9931 | 145.1672 | 363 Cheltenham Rd, Keysborough VIC 3173 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3KGP | Kings Park | VIC | -37.7428 | 144.7994 | 1 Victoria Cres, St Albans VIC 3021 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3LIL | Lilydale | VIC | -37.7584 | 145.3527 | 20 Hardy St, Lilydale VIC 3140 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3MTE | Mount Eliza | VIC | -38.1834 | 145.0906 | 63 Mount Eliza Way, Mount Eliza VIC 3930 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3NBA | North Balwyn | VIC | -37.7917 | 145.0928 | 269 Doncaster Rd, Balwyn North VIC 3104 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3MEA | Nunawading Depot | VIC | -37.8212 | 145.167 | 60 Terracotta Drive, Nunawading VIC 3131 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3MEB | Port Melbourne Depot | VIC | -37.8257 | 144.9055 | 282 Lorimer St, Port Melbourne VIC 3207 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3RES | Reservoir | VIC | -37.7134 | 145.0078 | 917 High St, Reservoir VIC 3073 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3RWO | Ringwood | VIC | -37.8149 | 145.2267 | 13 Ringwood St, Ringwood VIC 3134 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3SHP | Shepparton | VIC | -36.3804 | 145.3998 | 307-331 Wyndham St, Shepparton VIC 3630 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3SMR | South Morang | VIC | -37.6578 | 145.0759 | 153 Centenary Dr, Mill Park VIC 3082 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3STK | St Kilda | VIC | -37.8642 | 144.9841 | 62 Inkerman St, St Kilda VIC 3182 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3TNB | Thornbury | VIC | -37.7582 | 145.0004 | 739-741 High St, Thornbury VIC 3071 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3TAG | Traralgon | VIC | -38.1949 | 146.5373 | 7 Kay St, Traralgon VIC 3844 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3TMN | Tullamarine | VIC | -37.7051 | 144.8836 | 143-145 Melrose Dr, Tullamarine VIC 3043 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3WER | Werribee | VIC | -37.8958 | 144.6591 | 51-55 Market Rd, Werribee VIC 3030 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
3WHL | Wheelers Hill | VIC | -37.9025 | 145.161 | 535 Springvale Rd, Wheelers Hill VIC 3150 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
6APP | Applecross | WA | -32.0164 | 115.8384 | 101 Ardross St, Applecross WA 6153 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
6BSD | Bassendean | WA | -31.9049 | 115.9493 | 1 Wilson St, Bassendean WA 6054 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
6PEB | Bentley Depot | WA | -31.9995 | 115.9249 | 47 Charles Street, Bentley WA 6102 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
6CAN | Cannington | WA | -32.0172 | 115.9322 | 1329 Albany Hwy, Cannington WA 6107 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
6DBL | Doubleview | WA | -31.8986 | 115.7867 | 298 Scarborough Beach Road, Doubleview WA 6018 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
6GLT | Geraldton | WA | -28.7736 | 114.6103 | 15 Chapman Rd, Geraldton WA 6530 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
6HIL | Hilton | WA | -32.0628 | 115.7915 | 10-16 Chamberlain St, Hilton WA 6163 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
6KAT | Katanning | WA | -33.6895 | 117.5559 | 6 Richardson Street, Katanning WA 6317 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
6KEL | Kelmscott | WA | -32.1133 | 116.0138 | 2291 Albany Hwy, Kelmscott WA 6111 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
6MLO | Mullaloo | WA | -31.79 | 115.7565 | 1 Coral St, Craigie WA 6025 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
6PNJ | Pinjarra | WA | -32.6272 | 115.8737 | 13 Murray Street, Pinjarra WA 6208 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
6CGE | South Coogee | WA | -32.1755 | 115.7945 | 1022 Rockingham Rd, Wattleup WA 6166 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
6SUB | Subiaco | WA | -31.9498 | 115.8244 | 172 Rokeby Rd, Subiaco WA 6008 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying
6PEA | Wangara Depot | WA | -31.7918 | 115.8453 | 5 Prosperity Ave, Wangara WA 6065 | nbn.rinseout.org (POI list) + community geocode gist; verify before relying

## NewsSources
source_id | name | type | url | language | filter_keywords | enabled
gnews-dc-au | Google News: "data centre" Australia | rss | https://news.google.com/rss/search?q=%22data+centre%22+australia+when%3A7d&hl=en-AU&gl=AU&ceid=AU:en | en |  | TRUE
gnews-dc-au-2 | Google News: "data center" Australia | rss | https://news.google.com/rss/search?q=%22data+center%22+australia+when%3A7d&hl=en-AU&gl=AU&ceid=AU:en | en |  | TRUE
gnews-operators | Google News: key operators | rss | https://news.google.com/rss/search?q=(AirTrunk+OR+NEXTDC+OR+%22CDC+Data+Centres%22+OR+%22Firmus%22+OR+%22DigiCo%22+OR+%22Macquarie+Data+Centres%22)+when%3A7d&hl=en-AU&gl=AU&ceid=AU:en | en |  | TRUE
gnews-grid | Google News: data centre grid / AEMO / planning | rss | https://news.google.com/rss/search?q=%22data+centre%22+(AEMO+OR+Transgrid+OR+%22planning+approval%22+OR+%22State+Significant%22+OR+AusNet+OR+Powerlink)+when%3A7d&hl=en-AU&gl=AU&ceid=AU:en | en |  | TRUE
gnews-zh | Google News 中文：澳洲 数据中心 | rss | https://news.google.com/rss/search?q=%E6%B3%B3%E6%B4%B2+%E6%95%B0%E6%8D%AE%E4%B8%AD%E5%BF%83+when%3A7d&hl=zh-CN&gl=CN&ceid=CN:zh-Hans | zh |  | TRUE
dcd | Data Center Dynamics (filtered to Australia) | rss | https://www.datacenterdynamics.com/en/rss/ | en | Australia, Sydney, Melbourne, Brisbane, Perth, Canberra, AirTrunk, NEXTDC, CDC Data Centres, Firmus | TRUE
itnews | iTnews (filtered) | rss | https://www.itnews.com.au/RSS/rss.ashx | en | data centre, data center, AirTrunk, NEXTDC, CDC, hyperscale | TRUE
afr | AFR (Google News site query) | rss | https://news.google.com/rss/search?q=site%3Aafr.com+%22data+centre%22+when%3A7d&hl=en-AU&gl=AU&ceid=AU:en | en |  | TRUE

## Changelog
version_file | date | editor | notes
ADC_Master_20260915.xlsx | 2026-09-15 | Claude (initial seed) | Initial seed: 114 facilities, 29 operators, FED+8 jurisdictions, 122 infrastructure points, 121 NBN POIs, 8 news sources.
ADC_Master_20260915.xlsx | 2026-09-15 | Claude | Chinese text rewritten as professional DC-industry prose (proper nouns kept in English); operator backgrounds, regulatory overviews/steps and the national summary restructured as dot points.
ADC_Master_20261007.xlsx | 2026-10-07 |  | Refresh to 7 Oct 2026: sector sweep 15 Sep - 7 Oct
ADC_Master_20261007.xlsx | 2026-10-07 | Claude | Sector refresh 15 Sep - 7 Oct 2026: 20 facilities added (incl. backfill of pre-window gaps), 10 updated, 'Withdrawn' stage introduced, capacity_basis column added, Firmus Project Southgate figures retired after the CDC split, 4 operators added, 21 market moves, 8 regulatory changes and 14 step updates, new JLL/Transgrid market metrics, KPI tile control columns.
ADC_Master_20261012.xlsx | 2026-10-12 |  | Subtitle: drop the trailing 'one maintained source' / 一站式持续维护